## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Northpower
| Disclosure Date | 2025-06-23
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Northpower
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | F-5419-A | Mata |  | Ruakaka CB3 | 2024-04-02 08:44 | 45384.3639 | 2024-04-02 11:37 | 45384.4838 | 0.12447 | 0.0016224 | 104 | 7979 | Unplanned | Defective Equipment | FP 380845 Shutdown to replace HV fuses Tx X221 (faulty)
10 |  | O-406-C | Puwera |  | Maungatapere CB7 | 2024-04-02 09:07 | 45384.3799 | 2024-04-02 14:36 | 45384.6083 | 0.31821 | 0.00096721 | 62 | 20398 | Planned | Planned Interruption | Replace poles and crossarms
11 |  | O-640-C | Kensington |  | Alexander St CB8 | 2024-04-02 09:12 | 45384.3833 | 2024-04-02 14:40 | 45384.6111 | 0.62937 | 0.0019188 | 123 | 40344 | Planned | Planned Interruption | 123 ICP's advertised, OMS logged 89 (replaced Tx WC131 with Tx WC468 with 0 ICP's)
12 |  | O-541-C | Swamp North |  | Hikurangi CB1042 | 2024-04-03 09:05 | 45385.3785 | 2024-04-03 13:40 | 45385.5694 | 0.20163 | 0.00073321 | 47 | 12925 | Planned | Planned Interruption | Replace cross arms and HV fuses at Dsubs KB337, KB306 and HV links 6750
13 |  | F-5434-A | Kaiatea |  | Ngunguru CB1072 | 2024-04-03 19:23 | 45385.8076 | 2024-04-03 19:24 | 45385.8084 | 0.012402 | 0.010624 | 681 | 795 | Unplanned | Unknown | Tripped O/C - Unknown cause - F5 - Sw 720 FPI activated
14 |  | F-5437-A | Coast |  | Dargaville CB6 | 2024-04-04 08:06 | 45386.3377 | 2024-04-04 08:22 | 45386.3483 | 0.24626 | 0.016255 | 1042 | 15786 | Unplanned | Unknown | A & C Phase OC trip. F4. Closed & held after 15 min
15 |  | O-736-C | Coast |  | Dargaville CB6 | 2024-04-04 09:45 | 45386.4062 | 2024-04-04 17:04 | 45386.7111 | 0.29679 | 0.00078001 | 50 | 19025 | Planned | Planned Interruption | X arm replacements
16 |  | F-5455-A | Kensington |  | Alexander St CB8 | 2024-04-05 00:05 | 45387.0035 | 2024-04-05 00:21 | 45387.0147 | 0.18652 | 0.011513 | 738 | 11956 | Unplanned | Unknown | Trip EF - Unknown
17 |  | O-760-C | Wharekohe |  | Poroti CB1062 | 2024-04-05 09:34 | 45387.3986 | 2024-04-05 11:45 | 45387.4896 | 0.15123 | 0.0011544 | 74 | 9694 | Planned | Planned Interruption | Remove Knife links 8150KL. Remove OLD LS TX W133, DOF's and pole 54601
18 |  | F-5458-A | Taipuha |  | Mareretu CB1 | 2024-04-05 11:39 | 45387.4854 | 2024-04-05 12:55 | 45387.5382 | 0.10789 | 0.0014196 | 91 | 6916 | Unplanned | Defective Equipment | FP 380965 Cracked porcelain on DDO
19 |  | F-5470-A | Matapouri |  | Ngunguru CB1032 | 2024-04-05 23:48 | 45387.9917 | 2024-04-06 01:52 | 45388.0778 | 0.029562 | 0.0004524 | 29 | 1895 | Unplanned | Vegetation | FP 381053 - Gum Tree fell from slope into 11kV jumpers/ bushings/ HV Fuses
20 |  | F-5473-A | Access Rd |  | Ruawai CB1022 | 2024-04-06 07:20 | 45388.3059 | 2024-04-06 07:42 | 45388.3206 | 0.078656 | 0.0052416 | 336 | 5042 | Unplanned | Unknown | CB 1022 RWI Trip Overcurrent B & C. Reclosed & BTN.
21 |  | F-5476-A | Taipuha |  | Mareretu CB1 | 2024-04-06 09:43 | 45388.4048 | 2024-04-06 11:28 | 45388.4779 | 0.3906 | 0.0037128 | 238 | 25038 | Unplanned | Wildlife | Leech Road. Magpie found on pole top. Cause overcurrent trip. Removed & BTN
22 |  | O-649-C | Puwera |  | Maungatapere CB7 | 2024-04-08 09:04 | 45390.3778 | 2024-04-08 13:43 | 45390.5715 | 0.091401 | 0.0003276 | 21 | 5859 | Planned | Planned Interruption | Pole and Xarm replacements
23 |  | F-5515-A | Jordan Valley |  | Hikurangi CB1102 | 2024-04-09 03:36 | 45391.1499 | 2024-04-09 03:37 | 45391.1509 | 0.011294 | 0.0085801 | 550 | 724 | Unplanned | Unknown | CB 1102 HIK Trip & Close
24 |  | O-616-C | Access Rd |  | Ruawai CB1022 | 2024-04-09 09:03 | 45391.3771 | 2024-04-09 15:25 | 45391.6424 | 0.43503 | 0.0011388 | 73 | 27886 | Planned | Planned Interruption | X arm replacements
25 |  | O-12991-A | Waipu |  | Ruakaka CB2 | 2024-04-09 09:07 | 45391.3799 | 2024-04-09 14:38 | 45391.6097 | 0.91913 | 0.0027768 | 178 | 58918 | Planned | Planned Interruption | Xarm and pole replacements
|  | O-622-C | Jordan Valley |  | Hikurangi CB1102 | 2024-04-09 09:36 | 45391.4 | 2024-04-09 15:03 | 45391.6271 | 0.16324 | 0.0004992 | 32 | 10464 | Planned | Planned Interruption | Xarm & pole replacements
|  | O-397-C | Whakapara |  | Hikurangi CB1112 | 2024-04-10 09:05 | 45392.3785 | 2024-04-10 14:20 | 45392.5971 | 0.54009 | 0.001716 | 110 | 34621 | Planned | Planned Interruption | pole and x Arm replacements
|  | F-5530-A | Ararua |  | Mareretu CB2 | 2024-04-10 14:07 | 45392.5882 | 2024-04-10 14:24 | 45392.6 | 0.001326 | 7.8001e-05 | 5 | 85 | Unplanned | Defective Equipment | FP381151 Check & clean contacts on HV fuses
|  | F-5533-A | Mangawhai Heads |  | Mangawhai North CB1 | 2024-04-10 20:32 | 45392.8557 | 2024-04-10 21:21 | 45392.8896 | 1.0532 | 0.021575 | 1383 | 67513 | Unplanned | Unknown | 381171 - Tripped O/C A&B phase, F3 so patrolled and livened - Unknown cause
|  | O-13036-A | Swamp North |  | Hikurangi CB1042 | 2024-04-11 08:47 | 45393.366 | 2024-04-11 13:31 | 45393.5632 | 0.23924 | 0.00084241 | 54 | 15336 | Planned | Planned Interruption | Install New Tx KB 167 (CST live edit required)
|  | O-3541-B | Austin Road |  | Maunu CB1072 | 2024-04-11 09:01 | 45393.3757 | 2024-04-11 16:27 | 45393.6854 | 0.4105 | 0.00092041 | 59 | 26314 | Planned | Planned Interruption | Cut into existing 3core 35mm XLPE operation past Ashbury Height Subdivision between switch 7748 and 7749 Turn into newly instal
|  | O-748-C | Tangaihi |  | Ruawai CB1032 | 2024-04-11 09:13 | 45393.384 | 2024-04-11 15:37 | 45393.6507 | 0.041933 | 0.0001092 | 7 | 2688 | Planned | Planned Interruption | Install new Transformer K474 & Remove transformer K320
|  | F-5536-A | Coast |  | Dargaville CB6 | 2024-04-11 12:03 | 45393.5018 | 2024-04-11 19:31 | 45393.813 | 3.496 | 0.02379 | 1525 | 224100 | Unplanned | Vegetation | FP381218 Tree falled across lines - Sw 2120. Only 1 faultman available for several feeder faults. Isolated for Tree cutters.
|  | F-5539-A | North Dargaville |  | Dargaville CB1 | 2024-04-11 12:15 | 45393.5103 | 2024-04-11 15:37 | 45393.6507 | 0.39545 | 0.0040092 | 257 | 25349 | Unplanned | Vegetation | 381221 - Branch on line @ pole 24761
|  | F-5542-A | Tangowahine |  | Dargaville CB8 | 2024-04-11 12:32 | 45393.5222 | 2024-04-11 18:57 | 45393.7896 | 0.64806 | 0.00195 | 125 | 41542 | Unplanned | Unknown | 381230 -OC Trip BC.Shortage of fault staff for initial restoration.Recl 1504 found faulty, would not close,Marlon attended 12/04
|  | F-5548-A | Montgomery Ave |  | Onerahi CB8 | 2024-04-11 13:06 | 45393.546 | 2024-04-11 15:20 | 45393.6389 | 0.77342 | 0.016193 | 1038 | 49578 | Unplanned | Adverse Weather | FP381231 Sw 938 indicated fault ABC phase. Remotely liven to Sw 938, Patrol and liven remaining.
|  | F-5545-A | North Dargaville |  | Dargaville CB1 | 2024-04-11 13:08 | 45393.547 | 2024-04-11 15:48 | 45393.6582 | 0.33472 | 0.0020904 | 134 | 21456 | Unplanned | Defective Equipment | FP381229 Report of LV lines down on fence. De-energised 11kV remotely til staff could attend to isolate
|  | F-5572-A | Bickerstaff |  | Maungaturoto CB2 | 2024-04-11 13:54 | 45393.5793 | 2024-04-11 23:34 | 45393.9819 | 0.19216 | 0.01209 | 775 | 12318 | Unplanned | Defective Equipment | Tripped OC A & B Phase (F4) on F-5557-A Fault found later on F-5572-A (381259) - HV jumper off @ pole 16244
|  | F-5560-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-04-11 15:23 | 45393.6408 | 2024-04-12 06:28 | 45394.2694 | 0.59945 | 0.016755 | 1074 | 38426 | Unplanned | Vegetation | 381251 - Tripped twice on E/F - Patrolled and found stick on line, all clear
|  | F-5563-A | Turiwiri |  | Dargaville CB9 | 2024-04-11 15:54 | 45393.6628 | 2024-04-11 23:36 | 45393.9833 | 0.52611 | 0.027472 | 1761 | 33725 | Unplanned | Vegetation | 381249 - Trees in lines Between pole 21511 & 21512.
|  | F-5566-A | Town Dargaville |  | Dargaville CB3 | 2024-04-11 19:59 | 45393.8326 | 2024-04-12 01:58 | 45394.0819 | 0.32378 | 0.0011388 | 73 | 20755 | Unplanned | Defective Equipment | DA11 & DA48 lv back feed & DA 48 shut down to remove gen @ 2250hrs Kere has tied LV to all ICP's off Tx DA11 @ 0158hrs Kere
|  | O-643-C | Puwera |  | Maungatapere CB7 | 2024-04-12 10:04 | 45394.4194 | 2024-04-12 12:51 | 45394.5354 | 0.036473 | 0.0002184 | 14 | 2338 | Planned | Planned Interruption | X arm replacements
|  | F-5599-A | Pataua |  | Parua Bay CB1 | 2024-04-12 19:21 | 45394.8063 | 2024-04-12 22:39 | 45394.9437 | 0.0052728 | 6.2401e-05 | 4 | 338 | Unplanned | Defective Equipment | FP 381304-Replace HV Fuse carriers Tx OO242 (1 broken). 2nd shut to replace L9085 fuses & barrells (1 corroded)
|  | F-5605-A | Kaiwaka South |  | Kaiwaka CB1072 | 2024-04-13 12:01 | 45395.501 | 2024-04-13 17:21 | 45395.7229 | 0.26572 | 0.0022932 | 147 | 17033 | Unplanned | Vegetation | 381315 Tree across the line btween poles 33809 - 33810
|  | O-3547-B | Montgomery Ave |  | Onerahi CB8 | 2024-04-15 09:05 | 45397.3785 | 2024-04-15 15:12 | 45397.6333 | 0.81066 | 0.0024024 | 154 | 51965 | Planned | Planned Interruption | Replace pole and OH TX OP248 with Ground mount TX OP256
|  | O-775-C | Puwera |  | Maungatapere CB7 | 2024-04-15 09:49 | 45397.409 | 2024-04-15 12:28 | 45397.5194 | 0.22324 | 0.001404 | 90 | 14310 | Planned | Planned Interruption | Clear trees around lines from pole 46407 to pole 46411
|  | F-5620-A | Pataua |  | Parua Bay CB1 | 2024-04-15 15:47 | 45397.6575 | 2024-04-15 16:43 | 45397.6963 | 0.1717 | 0.0030732 | 197 | 11006 | Unplanned | Defective Equipment | 381375. Replace faulty DDOs
|  | F-5623-A | ToeToe Rd |  | Kioreroa CB7 | 2024-04-15 16:38 | 45397.693 | 2024-04-15 17:28 | 45397.7281 | 0.068641 | 0.0013572 | 87 | 4400 | Unplanned | Defective Equipment | 381346. Replace DDOs Tx X279
|  | O-3004-B | Whatatiri |  | Maungatapere CB8 | 2024-04-16 08:59 | 45398.3743 | 2024-04-16 14:31 | 45398.6049 | 0.68884 | 0.0020748 | 133 | 44156 | Planned | Planned Interruption | Replace Cross arms and refurbish Dsubs
|  | O-178-C | Coast |  | Dargaville CB6 | 2024-04-17 09:03 | 45399.3771 | 2024-04-17 16:05 | 45399.6701 | 1.9983 | 0.0047424 | 304 | 128098 | Planned | Planned Interruption | Remove switches 2158 & 2159. Install Switches 10162 &10163. Outages on DAR CB6 & CB7
|  | O-811-C | Swamp North |  | Hikurangi CB1042 | 2024-04-17 09:07 | 45399.3799 | 2024-04-17 14:53 | 45399.6201 | 0.54516 | 0.0015756 | 101 | 34946 | Planned | Planned Interruption | x Arm replacements, straighten poles, replace Tx
|  | O-12799-A | Whatatiri |  | Maungatapere CB8 | 2024-04-18 08:35 | 45400.3576 | 2024-04-18 13:17 | 45400.5535 | 0.58513 | 0.0020748 | 133 | 37508 | Planned | Planned Interruption | Replace Cross arms, HV transformer fuses at Dsub W420 W343 and connections. Work is between poles 60005,304795 and 59980
|  | O-652-C | King Road |  | Mangawhai North CB2 | 2024-04-18 10:25 | 45400.434 | 2024-04-18 13:59 | 45400.5826 | 0.0434 | 0.0002028 | 13 | 2782 | Planned | Planned Interruption | Network Maintenance - straighten pole 32475 and re-do connections at pole 32477
|  | F-5689-A | North River |  | Ruakaka CB7 | 2024-04-19 08:00 | 45401.3332 | 2024-04-19 12:56 | 45401.5389 | 0.70914 | 0.0041964 | 269 | 45457 | Unplanned | Defective Equipment | FP 381499 - Lines down between 44012 & 44016. Eye bolt ripped out of Crossarm.
|  | O-631-C | Puwera |  | Maungatapere CB7 | 2024-04-19 09:01 | 45401.3754 | 2024-04-19 13:23 | 45401.5574 | 0.077689 | 0.0002964 | 19 | 4980 | Planned | Planned Interruption | Replace pole 46034 and cross arms at numerous sites and connections at Dsub O129
|  | O-661-C | One Tree Point |  | Ruakaka CB6 | 2024-04-19 09:06 | 45401.3792 | 2024-04-19 13:12 | 45401.55 | 0.78671 | 0.003198 | 205 | 50430 | Planned | Planned Interruption | Replace cross arms and connections and replace pole 19949 and change TX RO366 from 30kVA to 50kVA
|  | F-5701-A | Titoki |  | Poroti CB1032 | 2024-04-20 09:43 | 45402.4048 | 2024-04-20 09:57 | 45402.4149 | 0.19408 | 0.013369 | 857 | 12441 | Unplanned | Unknown | O/C. Also took out part of DAR CB 8 due to network in abnormal state (SW2061 open, Sw2175 open)
|  | F-5710-A | Whakapara |  | Hikurangi CB1112 | 2024-04-20 15:27 | 45402.6439 | 2024-04-20 19:10 | 45402.7986 | 0.57337 | 0.011279 | 723 | 36754 | Unplanned | Third Party Interference | FP 381543. De-energised HV following report of car vs pole. LV pole 42411 replaced.
|  | F-5719-A | Coast |  | Dargaville CB6 | 2024-04-21 20:35 | 45403.8574 | 2024-04-22 00:46 | 45404.0319 | 0.17249 | 0.00068641 | 44 | 11057 | Unplanned | Defective Equipment | Rotten xarm
|  | F-5725-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-04-21 23:24 | 45403.9753 | 2024-04-22 09:55 | 45404.4132 | 0.95537 | 0.0072697 | 466 | 61241 | Unplanned | Wildlife | Curtis Point Rd - broken HV line Pole 29850. 2nd feeder fault - tripped again. Road closed Mountain Rd near pole 29817 by geeze
|  | F-5731-A | Poroti |  | Maungatapere CB2 | 2024-04-22 04:35 | 45404.1906 | 2024-04-22 06:05 | 45404.2535 | 0.4686 | 0.0096253 | 617 | 30038 | Unplanned | Unknown | 381553. Patrol lines after feeder fault. Nothing found & Line BTN
|  | F-5734-A | Turiwiri |  | Dargaville CB9 | 2024-04-22 06:34 | 45404.2738 | 2024-04-22 06:50 | 45404.2845 | 0.076472 | 0.0078625 | 504 | 4902 | Unplanned | Unknown | CB9 DAR Trip & 15 Min Close. Overcurrent A & B
|  | F-5737-A | Ararua |  | Mareretu CB2 | 2024-04-22 10:54 | 45404.4542 | 2024-04-22 12:25 | 45404.5174 | 0.39607 | 0.0043524 | 279 | 25389 | Unplanned | Defective Equipment | 381561. Isolate HV to repair spragged wires & install temp links for upcoming shutdown.
|  | F-5740-A | Ararua |  | Mareretu CB2 | 2024-04-22 11:35 | 45404.4826 | 2024-04-22 13:09 | 45404.5479 | 0.0014664 | 1.56e-05 | 1 | 94 | Unplanned | Defective Equipment | 1 x HV fuse blown. Isolated & replaced fuse holder due to damage.
|  | O-262-C | Hokianga Rd |  | Dargaville CB7 | 2024-04-23 09:02 | 45405.3763 | 2024-04-23 17:08 | 45405.7142 | 0.0075973 | 1.56e-05 | 1 | 487 | Planned | Planned Interruption | 11kV OHUG, connect 2x 11kV cables & liven. Cut away redundant overhead lines. Large work load resulting in late restoration.
|  | O-838-C | Ararua |  | Mareretu CB2 | 2024-04-23 09:11 | 45405.3826 | 2024-04-23 14:45 | 45405.6146 | 0.17641 | 0.0005304 | 34 | 11308 | Planned | Planned Interruption | Network Maintenance - replace pole 48576, hardware and change transformer like for like
|  | O-3574-B | Kaiwaka South |  | Kaiwaka CB1072 | 2024-04-23 09:12 | 45405.3836 | 2024-04-23 12:50 | 45405.5349 | 0.50314 | 0.0023088 | 148 | 32252 | Planned | Planned Interruption | Network Maintenance - REPLACE Sw3950
|  | F-5746-A | Springs Flat |  | Kamo CB1 | 2024-04-23 09:22 | 45405.3902 | 2024-04-23 09:37 | 45405.4009 | 0.099685 | 0.0084241 | 540 | 6390 | Unplanned | Unknown | A, B, C & E fault. Closed and held in after 15 mins.
|  | O-3616-B | Te Kopuru |  | Dargaville CB2 | 2024-04-23 09:48 | 45405.4083 | 2024-04-23 13:36 | 45405.5667 | 0.01067 | 4.68e-05 | 3 | 684 | Planned | Planned Interruption | LV Voltage Maintenance/Install
|  | O-667-C | 2nd Ave |  | Alexander St CB3 | 2024-04-23 10:32 | 45405.4389 | 2024-04-23 13:11 | 45405.5493 | 0.3299 | 0.0020748 | 133 | 21147 | Planned | Planned Interruption | Investigate High Partial discharge at switches 9010-9011-9012
|  | O-844-C | Swamp North |  | Hikurangi CB1042 | 2024-04-24 09:04 | 45406.3778 | 2024-04-24 12:54 | 45406.5375 | 0.36239 | 0.0015756 | 101 | 23230 | Planned | Planned Interruption | Replacing cross arms straightening poles & replacing TX. Repalcing Sw 679
|  | O-496-C | Tikipunga Hill |  | Tikipunga CB4 | 2024-04-24 09:05 | 45406.3785 | 2024-04-24 12:06 | 45406.5042 | 0.0084709 | 4.68e-05 | 3 | 543 | Planned | Planned Interruption | Install pole to reduce span length and raise LV arm. Remove temp switch @pole 32174 on completion of work.
|  | F-5758-A | Swamp North |  | Hikurangi CB1042 | 2024-04-24 21:52 | 45406.9113 | 2024-04-25 02:16 | 45407.0944 | 0.46935 | 0.011373 | 729 | 30086 | Unplanned | Defective Equipment | 381739. Line down at pole 38449. No cause found.
|  | F-5761-A | Swamp North |  | Hikurangi CB1042 | 2024-04-24 21:58 | 45406.915 | 2024-04-24 22:00 | 45406.9164 | 0.01429 | 0.0073945 | 474 | 916 | Unplanned | Defective Equipment | 381739. During fault on CB 1042 the FPIs for Sw 10010 should have activated as the lines down was past it. See CE Notes F-5761-A
|  | F-5770-A | One Tree Point |  | Ruakaka CB6 | 2024-04-26 14:51 | 45408.6188 | 2024-04-26 15:40 | 45408.6527 | 0.31213 | 0.0063961 | 410 | 20008 | Unplanned | Unknown | FP 381812. Patrolled before livening due to heavy fault current
|  | O-3622-B | Kaka St |  | Whangarei South CB1032 | 2024-04-28 09:01 | 45410.3757 | 2024-04-28 13:47 | 45410.5743 | 0.11365 | 0.0004056 | 26 | 7285 | Planned | Planned Interruption
|  | O-823-C | Hakaru |  | Kaiwaka CB1032 | 2024-04-30 09:05 | 45412.3785 | 2024-04-30 14:30 | 45412.6042 | 0.35997 | 0.0011076 | 71 | 23075 | Planned | Planned Interruption | hardware replacements and changing DSUB MC302 like for like
|  | O-544-C | ToeToe Rd |  | Kioreroa CB7 | 2024-04-30 09:12 | 45412.3833 | 2024-04-30 14:25 | 45412.6007 | 0.12695 | 0.0004056 | 26 | 8138 | Planned | Planned Interruption | Pole and cross arm replacement
|  | F-5785-A | Town Dargaville |  | Dargaville CB3 | 2024-04-30 16:04 | 45412.6696 | 2024-04-30 18:16 | 45412.7611 | 0.42755 | 0.014087 | 903 | 27407 | Unplanned | Third Party Interference | FP - 381956 / Event # - F3965949 - LV Lines down @ road crossing 32701 to 54143. Caused by Truck.
|  | O-3580-B | Kaiwaka South |  | Kaiwaka CB1072 | 2024-05-01 09:25 | 45413.3924 | 2024-05-01 15:30 | 45413.6458 | 0.039793 | 0.00010902 | 7 | 2555 | Planned | Planned Interruption | Network Maintenance - replace pole 33930 and transformer like for like
|  | O-3625-B | Paranui |  | Tikipunga CB6 | 2024-05-01 09:30 | 45413.3958 | 2024-05-01 10:53 | 45413.4535 | 0.020683 | 0.00024919 | 16 | 1328 | Planned | Planned Interruption | Network Extension upgrade tx from 75kVA to a 100kVA
|  | F-5803-A | Access Rd |  | Ruawai CB1022 | 2024-05-01 18:17 | 45413.7618 | 2024-05-01 21:12 | 45413.8833 | 0.1281 | 0.0018845 | 121 | 8225 | Unplanned | Defective Equipment | FP 382001 LV lines down across Rd - lv cut away between poles 44561 & 44562 - ICP 530929 previously electrially disconnected -
|  | O-3730-B | Fert. Works |  | Kioreroa CB6 | 2024-05-02 04:32 | 45414.1889 | 2024-05-02 04:48 | 45414.2 | 0.0017443 | 0.00010902 | 7 | 112 | Planned | Planned Interruption | Replacement HV fuses to correct sizing - down gradded to 50A- KN
|  | O-3631-B | Pataua |  | Parua Bay CB1 | 2024-05-02 09:01 | 45414.3757 | 2024-05-02 15:20 | 45414.6389 | 1.601 | 0.0050461 | 324 | 102798 | Planned | Planned Interruption | Improvements in Supply Quality - REMOVE Sw's 9885 & 9912, REPOSITION & INSTALL NEW Sw's 10134 & 10135
|  | O-3577-B | Waipu |  | Ruakaka CB2 | 2024-05-02 09:25 | 45414.3924 | 2024-05-02 13:29 | 45414.5618 | 0.20521 | 0.00084102 | 54 | 13176 | Planned | Planned Interruption | Network Maintenance replacing cross arms on poles 10383 and 10384
|  | O-3583-B | Dunns Rd |  | Ruawai CB1082 | 2024-05-02 09:36 | 45414.4 | 2024-05-02 10:47 | 45414.4493 | 0.087357 | 0.0012304 | 79 | 5609 | Planned | Planned Interruption | Reconfigure jumpers at pole 906579
|  | F-5812-A | North Dargaville |  | Dargaville CB1 | 2024-05-02 11:57 | 45414.4977 | 2024-05-02 18:19 | 45414.7632 | 0.28195 | 0.0023985 | 154 | 18103 | Unplanned | Third Party Interference | F3967151 / FP 382028 - Car vs pole
|  | O-3586-B | Whangarei Heads |  | Parua Bay CB3 | 2024-05-03 09:08 | 45415.3804 | 2024-05-03 14:18 | 45415.5958 | 1.0629 | 0.0034264 | 220 | 68248 | Planned | Planned Interruption | Network Maintenance replacing Cross arms
|  | O-3862-B | Tangowahine |  | Dargaville CB8 | 2024-05-03 09:36 | 45415.4 | 2024-05-03 13:33 | 45415.5646 | 0.23983 | 0.0010435 | 67 | 15399 | Planned | Planned Interruption | Replace damaged Recloser 1504
|  | O-3754-B | Onoke |  | Kamo CB8 | 2024-05-05 09:15 | 45417.3854 | 2024-05-05 14:54 | 45417.6208 | 0.35374 | 0.0010435 | 67 | 22713 | Planned | Planned Interruption | Upgrade ground mount D-Sub KV108 to 300kva. Replace concrete base.
|  | O-3751-B | Titoki |  | Poroti CB1032 | 2024-05-05 10:12 | 45417.4249 | 2024-05-05 11:39 | 45417.4854 | 0.17655 | 0.0020247 | 130 | 11336 | Planned | Planned Interruption | Isolate 11kv for Fulton hogan to replace Road sign near lines
|  | O-3652-B | Charles St |  | Kamo CB2 | 2024-05-06 09:00 | 45418.375 | 2024-05-06 13:13 | 45418.5507 | 0.14973 | 0.00059183 | 38 | 9614 | Planned | Planned Interruption | Network Maintenance - Replace LV arms at Pole 64319
|  | O-3655-B | Dunns Rd |  | Ruawai CB1082 | 2024-05-06 09:38 | 45418.4014 | 2024-05-06 14:03 | 45418.5854 | 0.11969 | 0.00045166 | 29 | 7685 | Planned | Planned Interruption | Drop lines from pole 45724 to pole 45725 for vegetation to drop tree.
|  | O-3775-B | Taipuha |  | Mareretu CB1 | 2024-05-06 09:51 | 45418.4104 | 2024-05-06 12:49 | 45418.534 | 0.016634 | 9.3447e-05 | 6 | 1068 | Planned | Planned Interruption | Liven new Tx B264
|  | F-5833-A | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2024-05-06 18:27 | 45418.769 | 2024-05-07 03:40 | 45419.1528 | 0.59613 | 0.005638 | 362 | 38276 | Unplanned | Third Party Interference | FP382234 / F-5833-A - Car V Pole (No trip,Pole broken at base)
|  | F-5839-A | Swamp North |  | Hikurangi CB1042 | 2024-05-06 20:33 | 45418.8562 | 2024-05-06 22:09 | 45418.9229 | 0.0029903 | 3.1149e-05 | 2 | 192 | Unplanned | Defective Equipment | FP382233 - F-5839-A. HV Jumper off @ Tx, Terminal bolt broken
|  | O-700-C | Swamp North |  | Hikurangi CB1042 | 2024-05-07 09:02 | 45419.3764 | 2024-05-07 13:59 | 45419.5826 | 0.68459 | 0.002305 | 148 | 43956 | Planned | Planned Interruption | Replace Cross arms and connections.
|  | O-3649-B | Puwera |  | Maungatapere CB7 | 2024-05-07 09:06 | 45419.3792 | 2024-05-07 15:06 | 45419.6292 | 0.072889 | 0.00020247 | 13 | 4680 | Planned | Planned Interruption | Network Maintenance - ARM & HARDWARE REPLACEMENTS
|  | O-3658-B | Marsden Pt |  | Ruakaka CB1 | 2024-05-07 09:08 | 45419.3806 | 2024-05-07 13:12 | 45419.55 | 0.65743 | 0.0026944 | 173 | 42212 | Planned | Planned Interruption | Network Extension install new TX on pole 16569 and disconnect the old LV overhead cable between poles 16570-332013 and run & ere
|  | O-3778-B | Charles St |  | Kamo CB2 | 2024-05-07 09:17 | 45419.3868 | 2024-05-07 14:56 | 45419.6222 | 0.20063 | 0.00059183 | 38 | 12882 | Planned | Planned Interruption | Upgrade transformer KT104
|  | O-3784-B | Langs Beach |  | Mangawhai North CB3 | 2024-05-07 09:45 | 45419.4062 | 2024-05-07 13:39 | 45419.5687 | 0.014578 | 6.2298e-05 | 4 | 936 | Planned | Planned Interruption | Network Extension - Replace pole 10718. Erect & liven 30kVA Tx RR353.
|  | O-3646-B | Pataua |  | Parua Bay CB1 | 2024-05-08 09:02 | 45420.3764 | 2024-05-08 15:12 | 45420.6333 | 0.47253 | 0.0012771 | 82 | 30340 | Planned | Planned Interruption | Network Maintenance - REPLACE POLE 24608 (TxPO117)
|  | O-703-C | Jordan Valley |  | Hikurangi CB1102 | 2024-05-08 09:09 | 45420.3811 | 2024-05-08 14:42 | 45420.6123 | 0.25921 | 0.00077873 | 50 | 16643 | Planned | Planned Interruption | Replace HV & LV cross arms.
|  | O-3694-B | Town Hikurangi |  | Hikurangi CB1082 | 2024-05-08 09:31 | 45420.3965 | 2024-05-08 15:17 | 45420.6368 | 0.3341 | 0.00096562 | 62 | 21452 | Planned | Planned Interruption | Network Maintenance Replace Transformer KS145 & run new HV & LV cables up pole
|  | F-5854-A | ToeToe Rd |  | Kioreroa CB7 | 2024-05-08 10:51 | 45420.4522 | 2024-05-08 12:01 | 45420.5007 | 0.13246 | 0.0033641 | 216 | 8505 | Unplanned | Defective Equipment | LV - ABC Lines down @ Pole 327366
|  | O-3664-B | Jordan Valley |  | Hikurangi CB1102 | 2024-05-09 09:03 | 45421.3771 | 2024-05-09 12:51 | 45421.5354 | 0.088775 | 0.00038936 | 25 | 5700 | Planned | Planned Interruption | Replace HV & LV cross arms, HV fuses and connections
|  | O-3865-B | Montgomery Ave |  | Onerahi CB8 | 2024-05-10 09:03 | 45422.3771 | 2024-05-10 15:57 | 45422.6646 | 0.61681 | 0.0014952 | 96 | 39604 | Planned | Planned Interruption | Replacing 11kv 400v poles 36555 & 36556
|  | O-3676-B | Puwera |  | Maungatapere CB7 | 2024-05-10 09:08 | 45422.3806 | 2024-05-10 12:50 | 45422.5347 | 0.093354 | 0.00042051 | 27 | 5994 | Planned | Planned Interruption | Network Maintenance replacing poles cross arms HV connections
|  | O-3667-B | Alamein Ave |  | Onerahi CB3 | 2024-05-10 09:11 | 45422.3826 | 2024-05-10 13:42 | 45422.5708 | 0.16461 | 0.00060741 | 39 | 10569 | Planned | Planned Interruption | Network Maintenance - LV ARM & HARDWARE REPLACEMENTS
|  | O-3793-B | Paparoa |  | Mareretu CB6 | 2024-05-10 09:36 | 45422.4 | 2024-05-10 13:41 | 45422.5701 | 0.045789 | 0.00018689 | 12 | 2940 | Planned | Planned Interruption | Reface pole 31131
|  | F-5878-A | Maungakaramea |  | Maungatapere CB3 | 2024-05-10 15:48 | 45422.6583 | 2024-05-10 16:31 | 45422.6882 | 0.040852 | 0.00095004 | 61 | 2623 | Unplanned | Defective Equipment | FP 382401 Broken Xarm @ pole 53736
|  | F-5884-A | Swamp North |  | Hikurangi CB1042 | 2024-05-13 08:12 | 45425.3419 | 2024-05-13 08:27 | 45425.3524 | 0.045992 | 0.0062921 | 404 | 2953 | Unplanned | Unknown | Sw 10010 indicated B phase. Sw 10010 closed after 15 minutes
|  | O-3679-B | Turiwiri |  | Dargaville CB9 | 2024-05-13 09:04 | 45425.3778 | 2024-05-13 15:04 | 45425.6278 | 0.17942 | 0.00049838 | 32 | 11520 | Planned | Planned Interruption | Replace HV poles and crossarms
|  | O-820-C | Whatatiri |  | Maungatapere CB8 | 2024-05-14 09:01 | 45426.3758 | 2024-05-14 14:22 | 45426.5983 | 0.50888 | 0.0015886 | 102 | 32674 | Planned | Planned Interruption | Replace cross arms at numerous sites and pole 60121
|  | O-3796-B | Titoki |  | Poroti CB1032 | 2024-05-14 10:04 | 45426.4194 | 2024-05-14 13:19 | 45426.5549 | 0.0060741 | 3.1149e-05 | 2 | 390 | Planned | Planned Interruption | Urgent Repairs - Transformer replacement & LV maintenance..
|  | F-5890-A | Waipu |  | Ruakaka CB2 | 2024-05-15 03:49 | 45427.1593 | 2024-05-15 07:01 | 45427.2924 | 0.90932 | 0.016338 | 1049 | 58385 | Unplanned | Vegetation | FP382507 - Found gum bark across 11kV Tx RR194
|  | F-5893-A | ToeToe Rd |  | Kioreroa CB7 | 2024-05-15 05:40 | 45427.2359 | 2024-05-15 08:09 | 45427.3396 | 0.76952 | 0.013908 | 893 | 49409 | Unplanned | Defective Equipment | 382522/ Jumper On Xarm. Stand off insulator installed (Fault found later on F-5902-A)
|  | O-847-C | Kaiatea |  | Ngunguru CB1072 | 2024-05-15 09:13 | 45427.384 | 2024-05-15 12:38 | 45427.5264 | 0.75349 | 0.0036756 | 236 | 48380 | Planned | Planned Interruption | Replant pole 59285 (908217)
|  | O-3973-B | Puwera |  | Maungatapere CB7 | 2024-05-15 09:26 | 45427.3931 | 2024-05-15 14:36 | 45427.608 | 0.091594 | 0.00029592 | 19 | 5881 | Planned | Planned Interruption | Acces through 11kv Only to work on 33kV
|  | F-5899-A | Pataua |  | Parua Bay CB1 | 2024-05-15 10:10 | 45427.4236 | 2024-05-15 13:23 | 45427.5576 | 0.081751 | 0.00095004 | 61 | 5249 | Unplanned | Defective Equipment | Line side HV jumper off at DDOs & also replaced DDOs
|  | F-5902-A | ToeToe Rd |  | Kioreroa CB7 | 2024-05-15 10:43 | 45427.4462 | 2024-05-15 13:23 | 45427.5576 | 0.12453 | 0.010715 | 688 | 7996 | Unplanned | Defective Equipment | 382522/ Jumper on Xarm @ pole 46122. Related to earlier tripping F-5893-A
|  | O-3799-B | North River |  | Ruakaka CB7 | 2024-05-16 09:09 | 45428.3812 | 2024-05-16 12:53 | 45428.5368 | 0.087217 | 0.00038936 | 25 | 5600 | Planned | Planned Interruption | Network Maintenance, change span of 7064 wire to Flourine
|  | O-3895-B | Swamp North |  | Hikurangi CB1042 | 2024-05-16 09:16 | 45428.3858 | 2024-05-16 14:01 | 45428.5839 | 0.24415 | 0.0008566 | 55 | 15676 | Planned | Planned Interruption | Network Maintenance cross arm replacements
|  | F-5917-A | Wairere |  | Mareretu CB5 | 2024-05-16 23:04 | 45428.9611 | 2024-05-16 23:05 | 45428.9619 | 0.0081455 | 0.0065101 | 418 | 523 | Unplanned | Unknown | Trip OC Phase BC FPI @ Sw 381 OC Phase AB
|  | F-5935-A | Town Hikurangi |  | Hikurangi CB1082 | 2024-05-17 15:22 | 45429.64 | 2024-05-17 15:51 | 45429.6605 | 0.25175 | 0.0085193 | 547 | 16164 | Unplanned | Defective Equipment | FP:382591 - Customer reported lines down. Jason Rhodes found broken guy wire.
|  | O-646-C | Treatment |  | Kioreroa CB2 | 2024-05-19 09:01 | 45431.3757 | 2024-05-19 14:19 | 45431.5965 | 1.2288 | 0.0039559 | 254 | 78900 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & HARDWARE REPLACEMENT
|  | O-3829-B | Bickerstaff |  | Maungaturoto CB2 | 2024-05-20 09:39 | 45432.402 | 2024-05-20 14:04 | 45432.5861 | 0.10893 | 0.0013238 | 85 | 6994 | Planned | Planned Interruption | Network Maintenance - replace 11kV fuse carriers. & Replace Tx DA237
|  | O-3685-B | Marua |  | Hikurangi CB1022 | 2024-05-21 09:06 | 45433.3792 | 2024-05-21 13:49 | 45433.5757 | 0.21597 | 0.00076315 | 49 | 13867 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms as per plan.
|  | O-793-C | Paranui |  | Tikipunga CB6 | 2024-05-21 09:15 | 45433.3854 | 2024-05-21 10:53 | 45433.4535 | 0.083947 | 0.0008566 | 55 | 5390 | Planned | Planned Interruption | Replace poles 51103 and 51104 to gain height
|  | F-6007-A | Turiwiri |  | Dargaville CB9 | 2024-05-21 17:13 | 45433.7174 | 2024-05-21 19:45 | 45433.8229 | 0.044979 | 0.00029592 | 19 | 2888 | Unplanned | Defective Equipment | FP 382710 Shutdown to repair blown HV jumper @ Tx J248
|  | F-6010-A | Te Kopuru |  | Dargaville CB2 | 2024-05-21 19:31 | 45433.8132 | 2024-05-21 19:47 | 45433.8242 | 0.11767 | 0.014874 | 955 | 7555 | Unplanned | Unknown | Tripped O/C B&C phase - Unknown cause - SCADA switching only
|  | O-3916-B | Waipu |  | Ruakaka CB2 | 2024-05-22 09:01 | 45434.3758 | 2024-05-22 13:25 | 45434.5589 | 0.50077 | 0.0019001 | 122 | 32153 | Planned | Planned Interruption | Network Maintenance replace cross arms and poles and transformer. Pole 10317.RR159.RR267.Pole 10351
|  | O-3985-B | Dunns Rd |  | Ruawai CB1082 | 2024-05-22 12:31 | 45434.5215 | 2024-05-22 13:55 | 45434.5799 | 0.0013083 | 1.5575e-05 | 1 | 84 | Planned | Planned Interruption | Network Maintenance - Replace Tx G142
|  | F-6031-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-05-23 06:38 | 45435.2761 | 2024-05-23 10:36 | 45435.4417 | 0.3893 | 0.0033952 | 218 | 24996 | Unplanned | Wildlife | FP -382784 Lines down Goose vs lines Pt Curtis
|  | O-3901-B | Titoki |  | Poroti CB1032 | 2024-05-23 09:02 | 45435.3764 | 2024-05-23 13:44 | 45435.5722 | 0.10541 | 0.00037379 | 24 | 6768 | Planned | Planned Interruption | Network Maintenance new guy wires straighten poles and new cross arms
|  | F-6034-A | Hakaru |  | Kaiwaka CB1032 | 2024-05-23 11:41 | 45435.4868 | 2024-05-23 13:05 | 45435.5451 | 0.087684 | 0.0025231 | 162 | 5630 | Unplanned | Unknown | Devich Rd - Repaired spragged 11kv line FP 382784
|  | O-4075-B | Fert. Works |  | Kioreroa CB6 | 2024-05-23 22:06 | 45435.9208 | 2024-05-24 01:08 | 45436.0472 | 0.27212 | 0.0014952 | 96 | 17472 | Planned | Planned Interruption | Transport high load from 17 Fraser street to 340 Port Road, Port Whangarei
|  | F-6037-A | Fert. Works |  | Kioreroa CB6 | 2024-05-24 05:56 | 45436.2472 | 2024-05-24 07:18 | 45436.3042 | 0.026819 | 0.00032706 | 21 | 1722 | Unplanned | Defective Equipment | FP382812 - Reinstate cable onto HV DDO Fuse
|  | O-4033-B | Tikipunga Hill |  | Tikipunga CB4 | 2024-05-24 09:06 | 45436.3792 | 2024-05-24 11:35 | 45436.4826 | 0.0069618 | 4.6724e-05 | 3 | 447 | Planned | Planned Interruption | Replace pole 908166 to gain correct ground clearance. This site has access issues and need to be done before it gets too wet.
|  | F-6046-A | Western Hills Dr |  | Alexander St CB7 | 2024-05-24 21:12 | 45436.8831 | 2024-05-25 03:59 | 45437.166 | 1.2043 | 0.016213 | 1041 | 77322 | Unplanned | Third Party Interference | FP382855 Replace pole damaged by vehicle Reg ZJ2940
|  | O-4078-B | Fert. Works |  | Kioreroa CB6 | 2024-05-25 22:02 | 45437.9181 | 2024-05-26 01:56 | 45438.0806 | 0.34987 | 0.0014952 | 96 | 22464 | Planned | Planned Interruption | Shut down for high load
|  | F-6049-A | Tangaihi |  | Ruawai CB1032 | 2024-05-26 15:25 | 45438.6422 | 2024-05-26 15:40 | 45438.6531 | 0.089257 | 0.0099365 | 638 | 5731 | Unplanned | Unknown | SCADA switching only Tripped O/C - Unknown cause
|  | O-841-C | Brynderwyn |  | Maungaturoto CB1 | 2024-05-27 09:13 | 45439.384 | 2024-05-27 12:29 | 45439.5201 | 0.0030526 | 1.5575e-05 | 1 | 196 | Planned | Planned Interruption | Network Maintenance - straighten pole 305359
|  | O-4003-B | Swamp North |  | Hikurangi CB1042 | 2024-05-27 09:29 | 45439.3951 | 2024-05-27 13:22 | 45439.5569 | 0.19596 | 0.00084102 | 54 | 12582 | Planned | Planned Interruption | Refurbish Dsub KB137 and replace HV arms on pole 38612. also replace LV arms at poles 37595, 38584 and 38582
|  | O-4069-B | King Road |  | Mangawhai North CB2 | 2024-05-28 12:32 | 45440.5221 | 2024-05-28 14:07 | 45440.5885 | 0.63793 | 0.0066659 | 428 | 40960 | Planned | Planned Interruption | Installing new automated Switch 10092 on pole 17639.
|  | O-3718-B | Turiwiri |  | Dargaville CB9 | 2024-05-29 09:05 | 45441.3785 | 2024-05-29 15:47 | 45441.6576 | 0.25044 | 0.00062298 | 40 | 16080 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-3721-B | Matapouri |  | Ngunguru CB1032 | 2024-05-29 09:28 | 45441.3946 | 2024-05-29 13:47 | 45441.5741 | 0.008052 | 3.1149e-05 | 2 | 517 | Planned | Planned Interruption | Replace HV cross arms at pole 58907/58908 and refurbish Dsub KT190
|  | F-6064-A | Kaiwaka South |  | Kaiwaka CB1072 | 2024-05-29 13:33 | 45441.5645 | 2024-05-29 13:49 | 45441.5755 | 0.12673 | 0.0080209 | 515 | 8137 | Unplanned | Unknown | F4 trip and close after 15 mins. No FPIs
|  | F-6067-A | Poroti |  | Maungatapere CB2 | 2024-05-29 15:24 | 45441.6416 | 2024-05-29 18:25 | 45441.7674 | 0.46051 | 0.022038 | 1415 | 29568 | Unplanned | Vegetation | FP 382990 - Branch in 11kV lines. Removed and relivened.
|  | F-6070-A | Parua Bay |  | Parua Bay CB2 | 2024-05-29 16:21 | 45441.6813 | 2024-05-30 12:52 | 45442.5361 | 1.5026 | 0.0091578 | 588 | 96476 | Unplanned | Vegetation | 383005 Lines down between poles 63976 & 13540 (SW 960 SCF)
|  | F-6073-A | Montgomery Ave |  | Onerahi CB8 | 2024-05-29 16:28 | 45441.6862 | 2024-05-29 17:12 | 45441.7165 | 0.32501 | 0.0074602 | 479 | 20868 | Unplanned | Vegetation | 383001 Trees across street light pole
|  | F-6082-A | Tangaihi |  | Ruawai CB1032 | 2024-05-29 17:20 | 45441.7222 | 2024-05-29 22:13 | 45441.9257 | 0.49683 | 0.0019935 | 128 | 31900 | Unplanned | Defective Equipment | 383006 - LV Xarm King bolt fail pole 62138, isolated OH section of LV, unable to complete LV repairs due to wind
|  | F-6085-A | Access Rd |  | Ruawai CB1022 | 2024-05-29 18:15 | 45441.7603 | 2024-05-30 02:33 | 45442.1062 | 1.1367 | 0.013425 | 862 | 72982 | Unplanned | Defective Equipment | FP - 383015 HV line down 14019 - 14020 Note: MTU CB 2 tripped at 2007hrs
|  | F-6088-A | Coast |  | Dargaville CB6 | 2024-05-29 18:33 | 45441.7731 | 2024-05-30 23:13 | 45442.9672 | 1.118 | 0.0025075 | 161 | 71782 | Unplanned | Vegetation | 383016 - HV Pole broken, HV Lines down & LV Pole replacement
|  | F-6112-A | Maungakaramea |  | Maungatapere CB3 | 2024-05-29 19:03 | 45441.7938 | 2024-05-30 03:41 | 45442.1535 | 0.07862 | 0.00095004 | 61 | 5048 | Unplanned | Defective Equipment | FP 383019 Repaired blown HV Jumper @ Links 875
|  | F-6091-A | Taipuha |  | Mareretu CB1 | 2024-05-29 19:42 | 45441.821 | 2024-05-29 23:50 | 45441.9934 | 0.76818 | 0.0064323 | 413 | 49323 | Unplanned | Wildlife | FP - 383034 - LA dangling around @ X307. Found bird at base of pole.
|  | F-6094-A | Ararua |  | Mareretu CB2 | 2024-05-29 20:07 | 45441.8382 | 2024-05-30 06:36 | 45442.275 | 5.3439 | 0.018456 | 1185 | 343118 | Unplanned | Defective Equipment | FP 385035 - 2x lines down between poles 21690 & 21689 - Backfeeding from switch 2077 to switch 2235 at time of tripping.
|  | F-6103-A | North Dargaville |  | Dargaville CB1 | 2024-05-29 20:21 | 45441.8478 | 2024-05-30 16:38 | 45442.6931 | 1.2925 | 0.020808 | 1336 | 82988 | Unplanned | Defective Equipment | 383039 Repaired lines down - pole 60974 (Broke at binder
|  | F-6139-A | Tangowahine |  | Dargaville CB8 | 2024-05-30 10:51 | 45442.4521 | 2024-05-30 14:51 | 45442.6188 | 0.037379 | 0.00015575 | 10 | 2400 | Unplanned | Defective Equipment | 382997 Repaired broken lines Kirikopuni Valley Rd
|  | F-6148-A | One Tree Point |  | Ruakaka CB6 | 2024-05-30 14:04 | 45442.5864 | 2024-05-30 17:44 | 45442.7389 | 0.83996 | 0.013581 | 872 | 53932 | Unplanned | Defective Equipment | 383076 Replaced 11kV insulator
|  | O-4087-B | Fraser |  | Kioreroa CB5 | 2024-05-30 20:41 | 45442.8618 | 2024-05-30 23:04 | 45442.9611 | 0.36435 | 0.0027255 | 175 | 23394 | Planned | Planned Interruption | High Load Transport
|  | F-6157-A | Mata |  | Ruakaka CB3 | 2024-05-31 09:25 | 45443.3924 | 2024-05-31 13:59 | 45443.5826 | 0.12802 | 0.00046724 | 30 | 8220 | Unplanned | Adverse Environment | 382904 Pole change & crossarms
|  | F-6166-A | Treatment |  | Kioreroa CB2 | 2024-06-01 11:34 | 45444.4819 | 2024-06-01 18:01 | 45444.7507 | 0.12051 | 0.00031139 | 20 | 7740 | Unplanned | Third Party Interference | 383138. Car Vs GM Tx WO256. Replaced & BTN
|  | F-6169-A | Titoki |  | Poroti CB1032 | 2024-06-01 14:50 | 45444.6181 | 2024-06-01 16:45 | 45444.6979 | 0.0017905 | 1.557e-05 | 1 | 115 | Unplanned | Unknown | 383143. Blown HV Fuse at L 8200. No Cause Found.
|  | F-6172-A | Kamo Town |  | Kamo CB7 | 2024-06-02 03:16 | 45445.1361 | 2024-06-02 13:47 | 45445.5743 | 0.0098245 | 1.557e-05 | 1 | 631 | Unplanned | Third Party Interference | 383147. Car Vs Tx KK159. Replaced & BTN
|  | O-3844-B | Turiwiri |  | Dargaville CB9 | 2024-06-04 09:05 | 45447.3785 | 2024-06-04 15:33 | 45447.6479 | 0.29601 | 0.00076291 | 49 | 19012 | Planned | Planned Interruption | Replacing 11kv pole and cross arms.
|  | F-6178-A | Bickerstaff |  | Maungaturoto CB2 | 2024-06-04 15:53 | 45447.6621 | 2024-06-04 17:58 | 45447.7486 | 0.3174 | 0.013359 | 858 | 20386 | Unplanned | Third Party Interference | (Salesforce down) Digger strike @ Tx D309 & Also loose connecion found sparking on Links 4028 on livening - Repaired
|  | F-6181-A | Treatment |  | Kioreroa CB2 | 2024-06-04 18:30 | 45447.7708 | 2024-06-04 20:33 | 45447.8562 | 0.088093 | 0.0007162 | 46 | 5658 | Unplanned | Defective Equipment | 382561. Emergency shut to Replace crossarm & increase conductor height.
|  | O-3886-B | Turiwiri |  | Dargaville CB9 | 2024-06-06 09:05 | 45449.3785 | 2024-06-06 15:32 | 45449.6472 | 0.29525 | 0.00076291 | 49 | 18963 | Planned | Planned Interruption | Replacing 11kv pole and cross arms.
|  | O-4045-B | Puwera |  | Maungatapere CB7 | 2024-06-06 09:06 | 45449.3792 | 2024-06-06 15:04 | 45449.6278 | 0.70232 | 0.0019618 | 126 | 45108 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & CONDUCTOR REPLACEMENT
|  | O-3880-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2024-06-06 09:20 | 45449.3889 | 2024-06-06 15:07 | 45449.6299 | 0.086443 | 0.00024911 | 16 | 5552 | Planned | Planned Interruption | Network Maintenance - Replace HV and LV hardware at pole 49213 TX C338
|  | O-4024-B | Wairere |  | Mareretu CB5 | 2024-06-06 09:33 | 45449.3979 | 2024-06-06 12:28 | 45449.5194 | 0.0027247 | 1.557e-05 | 1 | 175 | Planned | Planned Interruption | Transformer Upgrade - from 15kVA to 30kVA 3PH pole mount
|  | O-3889-B | Otangarei |  | Tikipunga CB7 | 2024-06-06 09:35 | 45449.3993 | 2024-06-06 11:32 | 45449.4806 | 0.16577 | 0.0014168 | 91 | 10647 | Planned | Planned Interruption | Network Maintenance Voltage indicators
|  | O-4201-B | Access Rd |  | Ruawai CB1022 | 2024-06-07 09:37 | 45450.4007 | 2024-06-07 11:07 | 45450.4632 | 0.018216 | 0.00020241 | 13 | 1170 | Planned | Planned Interruption | Lower HV Crossarm to extend circuit clearance to the 33KV line
|  | O-3928-B | Langs Beach |  | Mangawhai North CB3 | 2024-06-07 09:59 | 45450.416 | 2024-06-07 14:20 | 45450.5972 | 0.040637 | 0.0001557 | 10 | 2610 | Planned | Planned Interruption | P05D RMU servicing. Sw 4137, 4138, 4139, 4140, 4141, 4142, 4143
|  | F-6193-A | Coast |  | Dargaville CB6 | 2024-06-07 11:04 | 45450.4611 | 2024-06-07 15:38 | 45450.6514 | 0.2133 | 0.00077848 | 50 | 13700 | Unplanned | Defective Equipment | FP38278 Run LV under HV from pole 24977 - 24981 - Urgent
|  | F-6202-A | Whatatiri |  | Maungatapere CB8 | 2024-06-07 11:22 | 45450.4735 | 2024-06-07 12:14 | 45450.51 | 0.21741 | 0.015648 | 1005 | 13964 | Unplanned | Vegetation | FP383309 - Trip OC BC FPI at Sw 843 Phase ABC Same CB trip data on 2nd fault Pole 59970, branch found on HV Lines
|  | F-6199-A | Hotel |  | Poroti CB1052 | 2024-06-07 11:33 | 45450.4811 | 2024-06-07 13:44 | 45450.5722 | 0.011693 | 9.3418e-05 | 6 | 751 | Unplanned | Defective Equipment | 383292 - Blown top of jumper off DDO when attempting to close x1 HV F W428. Wider outage for Repair work (Fuses 8281)
|  | O-3919-B | North River |  | Ruakaka CB7 | 2024-06-07 12:02 | 45450.5011 | 2024-06-07 14:38 | 45450.6097 | 0.5622 | 0.0035966 | 231 | 36109 | Planned | Planned Interruption | Replace HV arm and install new DDO's and Liven TX RB333
|  | F-6205-A | Bickerstaff |  | Maungaturoto CB2 | 2024-06-07 16:24 | 45450.6833 | 2024-06-07 16:37 | 45450.6924 | 0.00040481 | 3.1139e-05 | 2 | 26 | Unplanned | Defective Equipment | FP 383326 HV fuse burnt in half
|  | F-6211-A | Montgomery Ave |  | Onerahi CB8 | 2024-06-09 08:18 | 45452.3457 | 2024-06-09 08:32 | 45452.3557 | 0.23263 | 0.016192 | 1040 | 14941 | Unplanned | Unknown | Trip & successful 15 min close.
|  | O-4057-B | Thelma Road |  | Mangawhai North CB4 | 2024-06-09 09:12 | 45452.3833 | 2024-06-09 14:04 | 45452.5861 | 0.15458 | 0.00052937 | 34 | 9928 | Planned | Planned Interruption | Transformer Upgrade from 100 to 150kVA pole mount type
|  | F-6217-A | Ararua |  | Mareretu CB2 | 2024-06-09 22:10 | 45452.9239 | 2024-06-10 03:09 | 45453.1312 | 0.39044 | 0.015118 | 971 | 25077 | Unplanned | Defective Equipment | 383348 Cracked insulator
|  | O-4093-B | Matapouri |  | Ngunguru CB1032 | 2024-06-10 09:20 | 45453.3889 | 2024-06-10 11:20 | 45453.4722 | 0.0037367 | 3.1139e-05 | 2 | 240 | Planned | Planned Interruption | Upgrade Tx from 15 kVA to 50kVA
|  | F-6226-A | Hakaru |  | Kaiwaka CB1032 | 2024-06-11 07:45 | 45454.3227 | 2024-06-11 08:04 | 45454.3361 | 0.2418 | 0.012845 | 825 | 15530 | Unplanned | Unknown | OC Trip Phase AB (No FPI indicaiton)
|  | O-4009-B | Puwera |  | Maungatapere CB7 | 2024-06-11 09:03 | 45454.3771 | 2024-06-11 14:21 | 45454.5979 | 0.089121 | 0.00028025 | 18 | 5724 | Planned | Planned Interruption | Network Maintenance - POLE STRAIGHTENS AND POLE REPLACEMENT
|  | O-3940-B | King Road |  | Mangawhai North CB2 | 2024-06-11 09:10 | 45454.3819 | 2024-06-11 14:19 | 45454.5965 | 0.062543 | 0.00020241 | 13 | 4017 | Planned | Planned Interruption | Network Maintenance - replace pole 32475 and re-do connections at pole 32477
|  | F-6232-A | Tangowahine |  | Dargaville CB8 | 2024-06-11 14:54 | 45454.6208 | 2024-06-11 15:13 | 45454.634 | 0.0073956 | 0.00038924 | 25 | 475 | Unplanned | Defective Equipment | FP 383408 - Rebind 2x HV insulators
|  | O-3943-B | Turiwiri |  | Dargaville CB9 | 2024-06-12 09:11 | 45455.3826 | 2024-06-12 14:49 | 45455.6173 | 0.29998 | 0.00088747 | 57 | 19267 | Planned | Planned Interruption | Network Maintenance. X-arm & pole changes. OH line alteration to rectify drain collapse
|  | O-4108-B | Tikipunga Hill |  | Tikipunga CB4 | 2024-06-12 12:08 | 45455.5056 | 2024-06-12 14:07 | 45455.5882 | 0.24272 | 0.0020396 | 131 | 15589 | Planned | Planned Interruption | Network Extension install new 15kVA TX as per 1c plan - tx KT435 not livened to due earthing.
|  | O-3946-B | Tikipunga Hill |  | Tikipunga CB4 | 2024-06-13 09:01 | 45456.3757 | 2024-06-13 15:10 | 45456.6319 | 0.44268 | 0.0012456 | 80 | 28432 | Planned | Planned Interruption | Network Maintenance Replacing 11kv 400v pole and Cross arms as per Map plain.
|  | O-4060-B | Titoki |  | Poroti CB1032 | 2024-06-13 09:38 | 45456.4014 | 2024-06-13 13:39 | 45456.5687 | 0.32648 | 0.0013857 | 89 | 20969 | Planned | Planned Interruption | Clear trees around lines from pole18345 to pole 18333
|  | F-6253-A | Maunu Road |  | Whangarei South CB1102 | 2024-06-14 07:08 | 45457.2972 | 2024-06-14 17:31 | 45457.7299 | 0.75893 | 0.0058853 | 378 | 48744 | Unplanned | Third Party Interference | 383512 - Car V HV Pole 36242,No Tripping Cut temp break to reduce outages.
|  | O-4102-B | One Tree Point |  | Ruakaka CB6 | 2024-06-14 09:05 | 45457.3785 | 2024-06-14 14:41 | 45457.6118 | 0.94165 | 0.0028025 | 180 | 60480 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms
|  | O-3802-B | Access Rd |  | Ruawai CB1022 | 2024-06-14 09:08 | 45457.3806 | 2024-06-14 13:16 | 45457.5528 | 0.13514 | 0.00054494 | 35 | 8680 | Planned | Planned Interruption | Replace HV conductor From pole 39716 to pole 39792
|  | F-6265-A | Tangaihi |  | Ruawai CB1032 | 2024-06-15 06:47 | 45458.2824 | 2024-06-15 07:04 | 45458.2942 | 0.10925 | 0.0099179 | 637 | 7017 | Unplanned | Unknown | Trip OC, Phase AC involved in fault
|  | F-6271-A | Ararua |  | Mareretu CB2 | 2024-06-15 08:42 | 45458.3623 | 2024-06-15 08:57 | 45458.3729 | 0.036371 | 0.0023822 | 153 | 2336 | Unplanned | Defective Equipment | 15 MIN reclose successful. Fault found later on F-6280-A ((HV jumper off Pole 21717)
|  | F-6277-A | North River |  | Ruakaka CB7 | 2024-06-15 09:57 | 45458.4146 | 2024-06-15 10:01 | 45458.4174 | 0.00024911 | 6.2279e-05 | 4 | 16 | Unplanned | Unknown | 383556 1 x HV fuse blown but opened all 3 - Shoemaker Rd
|  | F-6280-A | Ararua |  | Mareretu CB2 | 2024-06-15 17:16 | 45458.7194 | 2024-06-15 19:55 | 45458.83 | 0.12797 | 0.0023822 | 153 | 8219 | Unplanned | Defective Equipment | FP 383561 - HV jumper off pole 21727
|  | F-6286-A | Whatatiri |  | Maungatapere CB8 | 2024-06-15 21:18 | 45458.8874 | 2024-06-16 00:16 | 45459.0111 | 0.27494 | 0.00615 | 395 | 17659 | Unplanned | Adverse Environment | FP 383565 Building fire - Tx inside building, left de energised
|  | F-6289-A | Access Rd |  | Ruawai CB1022 | 2024-06-16 02:45 | 45459.1146 | 2024-06-16 08:05 | 45459.3368 | 0.37081 | 0.007489 | 481 | 23816 | Unplanned | Lightning | FP 383567_ Access Rd Lines down
|  | O-4135-B | Fraser |  | Kioreroa CB5 | 2024-06-16 09:38 | 45459.4014 | 2024-06-16 15:15 | 45459.6354 | 0.005247 | 1.557e-05 | 1 | 337 | Planned | Planned Interruption | Remove/decommission Tx WO297. Disconnect 11kv cable between WO227 and WO297 and abandon cable
|  | O-4129-B | Fert. Works |  | Kioreroa CB6 | 2024-06-16 10:11 | 45459.4243 | 2024-06-16 16:30 | 45459.6875 | 0.0059009 | 1.557e-05 | 1 | 379 | Planned | Planned Interruption | Replace 1Mva Tx WO300 with a 750kva.
|  | O-4249-B | Hakaru |  | Kaiwaka CB1032 | 2024-06-17 09:13 | 45460.384 | 2024-06-17 15:34 | 45460.6486 | 1.2576 | 0.0033008 | 212 | 80772 | Planned | Planned Interruption | Customer Work to upgrade MC229 from 100kva OH TX to 200kva pad mount Tx & other network maintenance.
|  | O-4177-B | Titoki |  | Poroti CB1032 | 2024-06-18 09:02 | 45461.3765 | 2024-06-18 13:43 | 45461.5718 | 0.18828 | 0.0006695 | 43 | 12093 | Planned | Planned Interruption | Network Maintenance - ARM & HARDWARE REPLACEMENT
|  | O-4138-B | North River |  | Ruakaka CB7 | 2024-06-18 09:33 | 45461.3979 | 2024-06-18 12:24 | 45461.5167 | 0.029287 | 0.00017127 | 11 | 1881 | Planned | Planned Interruption | Clear trees in 11kv lines from Pole #44051 to Pole #44052
|  | O-4147-B | Kaiwaka South |  | Kaiwaka CB1072 | 2024-06-18 10:04 | 45461.4194 | 2024-06-18 13:25 | 45461.559 | 0.034425 | 0.00017127 | 11 | 2211 | Planned | Planned Interruption | Network Extension - Upgrade Tx C411 from 50 to 100kVA pole mount type
|  | F-6301-A | Thelma Road |  | Mangawhai North CB4 | 2024-06-18 11:30 | 45461.4792 | 2024-06-18 11:36 | 45461.4833 | 0.00056051 | 9.3418e-05 | 6 | 36 | Unplanned | Other Cause | 383389 / Isolate for tap change.
|  | O-3949-B | Hakaru |  | Kaiwaka CB1032 | 2024-06-19 09:03 | 45462.3767 | 2024-06-19 14:08 | 45462.5891 | 0.076182 | 0.00024911 | 16 | 4893 | Planned | Planned Interruption | Network Maintenance - replace poles and hardware
|  | O-4141-B | Puwera |  | Maungatapere CB7 | 2024-06-19 09:03 | 45462.3771 | 2024-06-19 14:24 | 45462.6 | 0.30987 | 0.00096532 | 62 | 19902 | Planned | Planned Interruption | Network Maintenance replace cross arms and transformers straighten poles and redo connections
|  | F-6307-A | Tangaihi |  | Ruawai CB1032 | 2024-06-19 17:49 | 45462.7424 | 2024-06-19 18:36 | 45462.775 | 0.20782 | 0.0044218 | 284 | 13348 | Unplanned | Defective Equipment | Blown HV Jumper @ pole 11264 FP383690
|  | O-3961-B | Otangarei |  | Tikipunga CB7 | 2024-06-20 09:04 | 45463.3778 | 2024-06-20 19:16 | 45463.8028 | 0.94333 | 0.0015414 | 99 | 60588 | Planned | Planned Interruption | Network Maintenance - Cut away cable from SW7001 & Connect to New SW10144
|  | O-4150-B | Puwera |  | Maungatapere CB7 | 2024-06-20 09:10 | 45463.3819 | 2024-06-20 22:18 | 45463.9292 | 1.0733 | 0.0014324 | 92 | 68938 | Planned | Planned Interruption | HV & LV pole Cross arm replacement and replace pole 46425
|  | O-4288-B | ToeToe Rd |  | Kioreroa CB7 | 2024-06-20 09:11 | 45463.3826 | 2024-06-20 16:53 | 45463.7035 | 0.33808 | 0.00073177 | 47 | 21714 | Planned | Planned Interruption | Urgent Repairs. Tree to be cut between GBC poles 117 and 118.
|  | O-14629-A | Whakapara |  | Hikurangi CB1112 | 2024-06-23 23:42 | 45466.9875 | 2024-06-24 02:23 | 45467.0993 | 0.12784 | 0.00079405 | 51 | 8211 | Unplanned | Defective Equipment | FP 383782 Broken HV jumper pole 906135
|  | F-6463-A | Coast |  | Dargaville CB6 | 2024-06-24 07:24 | 45467.308 | 2024-06-24 14:21 | 45467.5979 | 0.69319 | 0.00246 | 158 | 44522 | Unplanned | Vegetation | FP 383787 Babylon coast Rd - Line down
|  | O-4210-B | Swamp North |  | Hikurangi CB1042 | 2024-06-24 09:14 | 45467.3847 | 2024-06-24 14:51 | 45467.6188 | 0.041976 | 0.00012456 | 8 | 2696 | Planned | Planned Interruption | Network Maintenance replace cross arms and reposition pole
|  | O-3736-B | Otangarei |  | Tikipunga CB7 | 2024-06-24 09:17 | 45467.3868 | 2024-06-24 13:14 | 45467.5514 | 0.28782 | 0.0012144 | 78 | 18486 | Planned | Planned Interruption | Cut away cables at SW7002 & connect to New SW10145
|  | O-4222-B | Tangaihi |  | Ruawai CB1032 | 2024-06-24 09:33 | 45467.3979 | 2024-06-24 13:52 | 45467.5778 | 0.0040325 | 1.557e-05 | 1 | 259 | Planned | Planned Interruption | Upgrade transformer & pole top connection for service line OHUG
|  | O-4162-B | Puwera |  | Maungatapere CB7 | 2024-06-25 09:04 | 45468.3778 | 2024-06-25 12:54 | 45468.5375 | 0.30797 | 0.001339 | 86 | 19780 | Planned | Planned Interruption | HV & LV pole Cross arm replacement and replace pole 46425
|  | O-4243-B | Jordan Valley |  | Hikurangi CB1102 | 2024-06-26 09:10 | 45469.3819 | 2024-06-26 15:02 | 45469.6264 | 0.060286 | 0.00017127 | 11 | 3872 | Planned | Planned Interruption | Network Extension upgrading from 50kVa to 100kVA transformer
|  | O-4306-B | Access Rd |  | Ruawai CB1022 | 2024-06-26 09:31 | 45469.3965 | 2024-06-26 14:24 | 45469.5997 | 0.53751 | 0.0018372 | 118 | 34523 | Planned | Planned Interruption | Replace pole 44561 with 12.5m Busck pole, Run new span of Flourine conductor to Lv pole 44562
|  | O-4246-B | Langs Beach |  | Mangawhai North CB3 | 2024-06-26 09:41 | 45469.4035 | 2024-06-26 14:56 | 45469.6222 | 1.1231 | 0.0035655 | 229 | 72135 | Planned | Planned Interruption | Replace poles 10598 and 10599. Relocate pole 10599 5m from current location
|  | F-6535-A | Marsden South |  | Bream Bay CB1111 | 2024-06-26 17:38 | 45469.7348 | 2024-06-26 17:54 | 45469.7457 | 0.024787 | 0.0015725 | 101 | 1592 | Unplanned | Unknown | Trip OC AB Phase
|  | F-6538-A | Titoki |  | Poroti CB1032 | 2024-06-26 22:56 | 45469.9555 | 2024-06-27 07:20 | 45470.3056 | 0.64068 | 0.0052314 | 336 | 41149 | Unplanned | Third Party Interference | 383912 278 Opouteke Rd - Car vs pole rego - LWL27
|  | F-6544-A | Town Hikurangi |  | Hikurangi CB1082 | 2024-06-27 06:34 | 45470.2737 | 2024-06-27 09:30 | 45470.3958 | 0.087642 | 0.00049823 | 32 | 5629 | Unplanned | Defective Equipment | Broken jumper and crucifix @ KS125. LV backfed from KS144 while repairs were made.
|  | O-4315-B | Maunu |  | Maunu CB1032 | 2024-06-27 09:02 | 45470.3764 | 2024-06-27 15:19 | 45470.6384 | 1.8969 | 0.005029 | 323 | 121830 | Planned | Planned Interruption | Network Maintenance. Replacing 400v Cross arms, Running 11kv conductor & Straightening Poles
|  | F-6559-A | Access Rd |  | Ruawai CB1022 | 2024-06-30 07:59 | 45473.3327 | 2024-06-30 08:16 | 45473.3446 | 0.047254 | 0.0052314 | 336 | 3035 | Unplanned | Unknown | Sw 2156 indicating fault - Livened remotely - all restored
|  | O-877-C | Whakapara |  | Hikurangi CB1112 | 2024-07-01 09:00 | 45474.3752 | 2024-07-01 15:04 | 45474.6281 | 0.15867 | 0.00043574 | 28 | 10196 | Planned | Planned Interruption | Remove pole 42015. Install new pole. Remove pole mount transformer KS130. Connect and liven new ground mount transformer KS567.
|  | O-4270-B | North Kaiwaka |  | Kaiwaka CB1022 | 2024-07-01 09:26 | 45474.3931 | 2024-07-01 14:42 | 45474.6125 | 0.068846 | 0.00021787 | 14 | 4424 | Planned | Planned Interruption | Upgrade Tx C184 from 50kVA to a 100kVA
|  | F-6589-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-07-01 10:49 | 45474.4507 | 2024-07-01 11:23 | 45474.4743 | 0.036509 | 0.0010738 | 69 | 2346 | Unplanned | Defective Equipment | Missing nut on the top crossarm pole 325279 - No FP isssued. Carried out with planned job, O-4270-B
|  | F-6565-A | Otonga |  | Hikurangi CB1032 | 2024-07-01 13:05 | 45474.5452 | 2024-07-01 13:21 | 45474.5561 | 0.39786 | 0.025288 | 1625 | 25566 | Unplanned | Unknown | T & C Paralleled wtih Whakapara fdr (planned job O-877-C) - no FPI's triggered
|  | O-4330-B | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-07-02 08:48 | 45475.3667 | 2024-07-02 13:38 | 45475.5678 | 0.53174 | 0.0018363 | 118 | 34169 | Planned | Planned Interruption | 33 kV line height mitigation 11kV isolation only for safety while working on 33kV lines.
|  | S-1802-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-07-02 08:49 | 45475.367 | 2024-07-02 13:39 | 45475.5685 | 0.53272 | 0.0018363 | 118 | 34232 | Planned | Planned Interruption | 33 kV line height mitigation 11kV isolation only for safety while working on 33kV lines.
|  | O-994-C | King Road |  | Mangawhai North CB2 | 2024-07-02 09:17 | 45475.3868 | 2024-07-02 14:54 | 45475.6208 | 0.0052444 | 1.5562e-05 | 1 | 337 | Planned | Planned Interruption | Network Extension - Upgrade transformer MC564 from 30kva to 300kva.
|  | F-6574-A | Matapouri |  | Ngunguru CB1032 | 2024-07-02 11:05 | 45475.4618 | 2024-07-02 11:15 | 45475.4688 | 0.0010893 | 0.00010893 | 7 | 70 | Unplanned | Other Cause | FP 384039 Changed tap settings on NT118
|  | O-928-C | Turiwiri |  | Dargaville CB9 | 2024-07-03 09:04 | 45476.3778 | 2024-07-03 15:03 | 45476.6271 | 0.27375 | 0.00076254 | 49 | 17591 | Planned | Planned Interruption | Replacing 11kv pole and cross arms.
|  | O-4261-B | Titoki |  | Poroti CB1032 | 2024-07-03 09:05 | 45476.3785 | 2024-07-03 13:58 | 45476.5819 | 0.33742 | 0.0011516 | 74 | 21682 | Planned | Planned Interruption | Replace HV & LV crossarms. Replace HV fuses at Dsub W222 Install Temp LV break at pole 342753
|  | O-4105-B | Paparoa |  | Mareretu CB6 | 2024-07-03 09:13 | 45476.384 | 2024-07-03 14:51 | 45476.6188 | 0.13676 | 0.00040461 | 26 | 8788 | Planned | Planned Interruption | Network Extension - Replace 11m pole 31146 with new 12.5m type.
|  | O-4420-B | Titoki |  | Poroti CB1032 | 2024-07-03 09:27 | 45476.3938 | 2024-07-03 13:27 | 45476.5604 | 0.037349 | 0.00015562 | 10 | 2400 | Planned | Planned Interruption | Clearing trees around 11kv lines
|  | F-6583-A | Ararua |  | Mareretu CB2 | 2024-07-03 12:24 | 45476.5169 | 2024-07-03 13:13 | 45476.5506 | 0.11559 | 0.002381 | 153 | 7428 | Unplanned | Defective Equipment | 384072 - Urgent shut to replace Xarm - Missing nut Insulator Pin
|  | O-4207-B | Titoki |  | Poroti CB1032 | 2024-07-04 09:03 | 45477.3771 | 2024-07-04 15:10 | 45477.6319 | 0.14278 | 0.00038905 | 25 | 9175 | Planned | Planned Interruption | Refurbish Dsubs TW150 and TW162
|  | O-4276-B | Swamp North |  | Hikurangi CB1042 | 2024-07-04 09:09 | 45477.3812 | 2024-07-04 13:00 | 45477.5417 | 0.59315 | 0.0025677 | 165 | 38115 | Planned | Planned Interruption | Replace HV and LV cross arms and refurbish Dsub KB147
|  | O-1054-C | North Dargaville |  | Dargaville CB1 | 2024-07-04 10:16 | 45477.4278 | 2024-07-04 15:30 | 45477.6458 | 0.13682 | 0.00043574 | 28 | 8792 | Unplanned | Defective Equipment | Urgent Repairs - Replace transformer pole due to spalling, leaking oil & condition of structure. Continue with LV once pole rep
|  | O-4165-B | One Tree Point |  | Ruakaka CB6 | 2024-07-08 09:09 | 45481.3812 | 2024-07-08 17:00 | 45481.7083 | 0.0073297 | 1.5562e-05 | 1 | 471 | Planned | Planned Interruption | NAR 5860 - cancelled part way through due to sw 5178 position indicator.
|  | O-4345-B | Hakaru |  | Kaiwaka CB1032 | 2024-07-08 09:38 | 45481.4011 | 2024-07-08 12:47 | 45481.5324 | 0.27959 | 0.0014784 | 95 | 17966 | Planned | Planned Interruption | Clear trees around 11kv lines from pole 45865 to pole 45864
|  | O-634-C | Titoki |  | Poroti CB1032 | 2024-07-08 10:18 | 45481.429 | 2024-07-08 13:23 | 45481.5576 | 0.37473 | 0.0020231 | 130 | 24080 | Planned | Planned Interruption | Replace HV cross arm at pole 50799 and refurbish Dsub W159
|  | F-6607-A | One Tree Point |  | Ruakaka CB6 | 2024-07-08 13:19 | 45481.5549 | 2024-07-08 17:00 | 45481.7083 | 0.0068784 | 3.1124e-05 | 2 | 442 | Unplanned | Defective Equipment | Faulty switch position indicator - Found during carrying out planned work NAR 5860
|  | O-4231-B | Waipu |  | Ruakaka CB2 | 2024-07-09 09:01 | 45482.3757 | 2024-07-09 13:09 | 45482.5478 | 1.0571 | 0.004264 | 274 | 67925 | Planned | Planned Interruption | Network Maintenance replacing cross arms and poles
|  | F-6613-A | One Tree Point |  | Ruakaka CB6 | 2024-07-09 10:27 | 45482.4354 | 2024-07-09 15:32 | 45482.6472 | 0.014177 | 4.6686e-05 | 3 | 911 | Unplanned | Defective Equipment | Replaced faulty RMU
|  | O-4435-B | Maungakaramea |  | Maungatapere CB3 | 2024-07-09 13:44 | 45482.5722 | 2024-07-09 15:10 | 45482.6319 | 0.073608 | 0.00085591 | 55 | 4730 | Planned | Planned Interruption | Network Maintenance Fit Neutral lugs flat
|  | F-6616-A | Fert. Works |  | Kioreroa CB6 | 2024-07-09 22:13 | 45482.9257 | 2024-07-10 00:39 | 45483.0274 | 0.17776 | 0.0012138 | 78 | 11423 | Unplanned | Defective Equipment | FP 384273 repair damaged conductor at pole 26039 causing arcing at pole
|  | O-4390-B | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-07-10 08:40 | 45483.3611 | 2024-07-10 14:36 | 45483.6083 | 1.7082 | 0.0054623 | 351 | 109767 | Planned | Planned Interruption | Improve 33 kV line height mitigation
|  | O-916-C | KAI - MWI 33kV |  | Kaiwaka CB52 | 2024-07-11 22:03 | 45484.9187 | 2024-07-12 05:10 | 45485.2153 | 17.8401 | 0.045472 | 2922 | 1146388 | Planned | Planned Interruption | Network Maintenance - replacing hardware between poles 17740 and 17651/21289
|  | O-931-C | Swamp North |  | Hikurangi CB1042 | 2024-07-12 09:37 | 45485.4007 | 2024-07-12 10:04 | 45485.4194 | 0.0021009 | 7.781e-05 | 5 | 135 | Planned | Planned Interruption | Install guy 33kv guy design insulators
|  | O-979-C | Tangowahine |  | Dargaville CB8 | 2024-07-12 11:02 | 45485.4597 | 2024-07-12 12:05 | 45485.5035 | 0.0039216 | 6.2248e-05 | 4 | 252 | Planned | Planned Interruption | Replace 11kv guy wire
|  | O-973-C | Fert. Works |  | Kioreroa CB6 | 2024-07-14 09:05 | 45487.3785 | 2024-07-14 15:39 | 45487.6521 | 0.079709 | 0.00020231 | 13 | 5122 | Planned | Planned Interruption | Replace HT fuses 9048 and 9096. Replace 11kv cable between fuses 9048 and Tx WO242. Upgrade Tx WO242 from a 200kva to a 500kva.
|  | O-4408-B | Whakapara |  | Hikurangi CB1112 | 2024-07-15 09:55 | 45488.4132 | 2024-07-15 11:19 | 45488.4715 | 0.039216 | 0.00046686 | 30 | 2520 | Planned | Planned Interruption | Fit neutral lugs flat, paint
|  | O-4066-B | Puwera |  | Maungatapere CB7 | 2024-07-16 09:04 | 45489.3778 | 2024-07-16 15:12 | 45489.6333 | 0.35506 | 0.00096485 | 62 | 22816 | Planned | Planned Interruption | Network Maintenance replace cross arms and transformers straighten poles and redo connections
|  | F-6664-A | Coast |  | Dargaville CB6 | 2024-07-17 04:27 | 45490.1852 | 2024-07-17 10:19 | 45490.4299 | 0.56926 | 0.0046686 | 300 | 36580 | Unplanned | Defective Equipment | FP 384538 Tripped EF - Replaced polymer at pole 15747
|  | O-886-C | One Tree Point |  | Ruakaka CB6 | 2024-07-18 09:05 | 45491.3785 | 2024-07-18 12:59 | 45491.541 | 0.40057 | 0.0017118 | 110 | 25740 | Planned | Planned Interruption | Ruakaka CB6 : Takahiwai Rd : Network Maintenance
|  | O-4264-B | Titoki |  | Poroti CB1032 | 2024-07-18 09:14 | 45491.3847 | 2024-07-18 13:56 | 45491.5806 | 0.14921 | 0.00052911 | 34 | 9588 | Planned | Planned Interruption | Replace cross arms and refurbish Dsub P194
|  | O-4441-B | Kaiatea |  | Ngunguru CB1072 | 2024-07-18 09:28 | 45491.3944 | 2024-07-18 10:42 | 45491.4458 | 0.055276 | 0.00074698 | 48 | 3552 | Planned | Planned Interruption | Network Maintenance Fit neutral lugs flush
|  | F-6688-A | Tangaihi |  | Ruawai CB1032 | 2024-07-18 12:13 | 45491.509 | 2024-07-18 15:43 | 45491.6549 | 0.013197 | 0.00017118 | 11 | 848 | Unplanned | Defective Equipment | FP 384521 - Replaced LV tx fuses & ampacts
|  | F-6700-A | Kaiatea |  | Ngunguru CB1072 | 2024-07-19 07:45 | 45492.3229 | 2024-07-19 08:01 | 45492.3338 | 0.071461 | 0.010613 | 682 | 4592 | Unplanned | Unknown | Trip & close to Sw 720. 15 min close on Sw 720 due to All FPIs activating.
|  | O-1003-C | Ararua |  | Mareretu CB2 | 2024-07-19 09:09 | 45492.3812 | 2024-07-19 14:33 | 45492.6062 | 0.12605 | 0.00038905 | 25 | 8100 | Planned | Planned Interruption | Network Maintenance - Replacement of LV X-Arms & reconductoring works below 11kV circuit
|  | O-4369-B | Titoki |  | Poroti CB1032 | 2024-07-19 09:18 | 45492.3875 | 2024-07-19 13:32 | 45492.5639 | 0.17392 | 0.00068473 | 44 | 11176 | Planned | Planned Interruption | Replace HV X arms
|  | F-6706-A | Three Mile Bush |  | Kamo CB3 | 2024-07-19 13:53 | 45492.5785 | 2024-07-19 16:53 | 45492.7035 | 1.1018 | 0.0065205 | 419 | 70800 | Unplanned | Defective Equipment | 384641. Outage to top up oil in RMU and find reason for leak.
|  | F-6712-A | Whatatiri |  | Maungatapere CB8 | 2024-07-20 12:52 | 45493.5361 | 2024-07-20 13:23 | 45493.5575 | 0.12588 | 0.009664 | 621 | 8089 | Unplanned | Unknown | No Fault Found. BTN
|  | F-6718-A | Te Kopuru |  | Dargaville CB2 | 2024-07-20 17:21 | 45493.7232 | 2024-07-20 17:36 | 45493.7337 | 0.12686 | 0.014691 | 944 | 8152 | Unplanned | Unknown | Trip EF A B & C. FPIs at Sw 2255 activated. BTN
|  | O-946-C | Treatment |  | Kioreroa CB2 | 2024-07-21 06:12 | 45494.2583 | 2024-07-21 13:49 | 45494.5757 | 0.092547 | 0.00071585 | 46 | 5947 | Planned | Planned Interruption | - Replace DOF's 9018 and assosiated hardware. - Straight joint 11kv cable feeding WO191A in the ground
|  | O-4375-B | Titoki |  | Poroti CB1032 | 2024-07-22 09:02 | 45495.3764 | 2024-07-22 12:02 | 45495.5014 | 0.019608 | 0.00010893 | 7 | 1260 | Planned | Planned Interruption | Replace HV cross arms
|  | F-6727-A | Swamp North |  | Hikurangi CB1042 | 2024-07-22 17:29 | 45495.7283 | 2024-07-22 17:43 | 45495.7385 | 0.092329 | 0.0063026 | 405 | 5933 | Unplanned | Unknown | Tripped O/C & closed after 15mins - Unknown
|  | O-4378-B | North River |  | Ruakaka CB7 | 2024-07-23 09:04 | 45496.3778 | 2024-07-23 14:43 | 45496.6132 | 0.29015 | 0.00085591 | 55 | 18645 | Planned | Planned Interruption | Refurbish Dub RB120, replace Links 531 and replace cross arms at various poles. Replace LV pole 43770
|  | O-985-C | Ruatangata |  | Kamo CB6 | 2024-07-24 09:01 | 45497.3757 | 2024-07-24 14:05 | 45497.5868 | 0.39739 | 0.0013072 | 84 | 25536 | Planned | Planned Interruption | Network Extension Upgrade tx from 100kVA to 150kVA pole mounted transformer and install new HV arm and raise LV arm
|  | O-4414-B | Titoki |  | Poroti CB1032 | 2024-07-24 09:08 | 45497.3806 | 2024-07-24 14:17 | 45497.5951 | 0.53376 | 0.0017274 | 111 | 34299 | Planned | Planned Interruption | Replace HV cross arms
|  | O-964-C | Dunns Rd |  | Ruawai CB1082 | 2024-07-24 13:10 | 45497.5486 | 2024-07-24 15:06 | 45497.6292 | 0.052351 | 0.0004513 | 29 | 3364 | Planned | Planned Interruption | Install 2x new pole mount transformers G281 & G282
|  | O-4384-B | Cairnfield Rd |  | Tikipunga CB5 | 2024-07-25 09:06 | 45498.3792 | 2024-07-25 13:52 | 45498.5778 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Network Maintenance - 2 POLE Tx STRUCTURE REPLACEMENT. OH/UG CONVERSION OF Tx WC115 TO NEW Tx WC245
|  | O-967-C | Coast |  | Dargaville CB6 | 2024-07-25 09:22 | 45498.3903 | 2024-07-25 11:51 | 45498.4934 | 0.20108 | 0.0013539 | 87 | 12921 | Planned | Planned Interruption | Network Extension - Replace11kV x-arm & Install HV fuse links 10186 for transformer L300.
|  | O-4381-B | Thelma Road |  | Mangawhai North CB4 | 2024-07-25 09:52 | 45498.4111 | 2024-07-25 13:20 | 45498.5556 | 0.025895 | 0.0001245 | 8 | 1664 | Planned | Planned Interruption | Transformer Upgrade - upgrade transformer from 50kva to 100kva
|  | F-6775-A | Ararua |  | Mareretu CB2 | 2024-07-25 22:19 | 45498.9299 | 2024-07-26 01:10 | 45499.0486 | 0.074511 | 0.00043574 | 28 | 4788 | Unplanned | Third Party Interference | FP 384823 - Replace damaged pole
|  | O-4297-B | Waipu |  | Ruakaka CB2 | 2024-07-26 09:39 | 45499.4021 | 2024-07-26 16:01 | 45499.6674 | 1.4381 | 0.0038905 | 250 | 92414 | Planned | Planned Interruption | HV/LV Arm and hardware replacements. Replace Tx RB101 - Delay in livening ICPs due to late start (High feeder loading)
|  | F-6781-A | Kaiatea |  | Ngunguru CB1072 | 2024-07-26 09:55 | 45499.4132 | 2024-07-26 11:37 | 45499.484 | 0.0063493 | 6.2248e-05 | 4 | 408 | Unplanned | Other Cause | 384604 - Raise Low HV Lines @ road crossing (Temp break installed for isolation)
|  | F-6784-A | Taipuha |  | Mareretu CB1 | 2024-07-26 11:21 | 45499.4729 | 2024-07-26 12:29 | 45499.5201 | 0.0031747 | 4.6686e-05 | 3 | 204 | Unplanned | Defective Equipment | 384834 - Repair buckarm at transformer B194 @ 248 Swamp Road
|  | F-6787-A | Otonga |  | Hikurangi CB1032 | 2024-07-27 07:33 | 45500.3145 | 2024-07-27 12:29 | 45500.5201 | 0.013819 | 4.6686e-05 | 3 | 888 | Unplanned | Wildlife | 2 x HV fuses blown due to swan.
|  | F-6790-A | Wairere |  | Mareretu CB5 | 2024-07-28 03:00 | 45501.125 | 2024-07-28 03:16 | 45501.1359 | 0.065983 | 0.0065205 | 419 | 4240 | Unplanned | Unknown | Trip OC AB - FPI at Swith 381 Phase BC
|  | F-6793-A | Te Kopuru |  | Dargaville CB2 | 2024-07-28 17:27 | 45501.7271 | 2024-07-28 19:59 | 45501.8326 | 0.042578 | 0.00028012 | 18 | 2736 | Unplanned | Defective Equipment | 384868/ Replace Faulty Xarms & Insulators. 15943 & 15944
|  | O-991-C | North River |  | Ruakaka CB7 | 2024-07-29 09:14 | 45502.3847 | 2024-07-29 13:42 | 45502.5708 | 0.16265 | 0.00060692 | 39 | 10452 | Planned | Planned Interruption | Replace HV cross arms and refurbish Dsub RB230 @ pole 39290
|  | F-6802-A | Tangaihi |  | Ruawai CB1032 | 2024-07-29 11:30 | 45502.4792 | 2024-07-29 11:43 | 45502.4882 | 0.00060692 | 4.6686e-05 | 3 | 39 | Unplanned | Vegetation | FP 384900 Tree over HV line, not touching @ pole 14600 - Isolate only
|  | O-4426-B | Maunu |  | Maunu CB1032 | 2024-07-29 13:21 | 45502.5563 | 2024-07-29 14:34 | 45502.6069 | 0.034081 | 0.00046686 | 30 | 2190 | Planned | Planned Interruption | Network Maintenance Fit neutral lugs flush
|  | O-889-C | North River |  | Ruakaka CB7 | 2024-07-30 09:02 | 45503.3765 | 2024-07-30 13:31 | 45503.5629 | 0.3968 | 0.0014784 | 95 | 25498 | Planned | Planned Interruption | Refurbish Dsubs RB164 and RB166 and replace HV and LV cross arms
|  | O-1006-C | Thelma Road |  | Mangawhai North CB4 | 2024-07-30 09:27 | 45503.3938 | 2024-07-30 10:45 | 45503.4479 | 0.1493 | 0.0019141 | 123 | 9594 | Planned | Planned Interruption | Network Maintenance - Installed T/Break@ Pole 312091, Disconnect cable from SW4184
|  | O-1021-C | Hokianga Rd |  | Dargaville CB7 | 2024-07-30 09:40 | 45503.4028 | 2024-07-30 14:31 | 45503.6049 | 0.64758 | 0.0022254 | 143 | 41613 | Planned | Planned Interruption | 11kV line alteration to facilitate relocation of DA44 into the berm (install new HV Fuses)
|  | O-4462-B | Whangarei Heads |  | Parua Bay CB3 | 2024-07-31 09:03 | 45504.3771 | 2024-07-31 15:28 | 45504.6444 | 0.9119 | 0.0031747 | 204 | 58598 | Planned | Planned Interruption | Replacing Transformer PO274 & Pole 24497
|  | O-4429-B | Brynderwyn |  | Maungaturoto CB1 | 2024-07-31 09:06 | 45504.3792 | 2024-07-31 13:16 | 45504.5528 | 0.085591 | 0.00034236 | 22 | 5500 | Planned | Planned Interruption | Network Maintenance - replace pole 48179 and hardware
|  | O-4489-B | Jordan Valley |  | Hikurangi CB1102 | 2024-07-31 09:08 | 45504.3806 | 2024-07-31 12:41 | 45504.5285 | 0.082868 | 0.00038905 | 25 | 5325 | Planned | Planned Interruption | Network Extension install new transformer KR309
|  | O-1009-C | Puwera |  | Maungatapere CB7 | 2024-07-31 09:28 | 45504.3944 | 2024-07-31 14:06 | 45504.5875 | 0.12792 | 0.00046686 | 30 | 8220 | Planned | Planned Interruption | Refurbish Dsub X228 and replace HV & LV cross arms at various sites
|  | O-1012-C | Thelma Road |  | Mangawhai North CB4 | 2024-07-31 09:31 | 45504.3965 | 2024-07-31 16:47 | 45504.6993 | 0.29807 | 0.00068473 | 44 | 19154 | Planned | Planned Interruption | Network Maintenance - Disconnect cables from Sw 4181, SW4182 and SW4183 , trifurcate and connect into new switch unit
|  | F-6826-A | Jordan Valley |  | Hikurangi CB1102 | 2024-07-31 15:04 | 45504.6278 | 2024-07-31 19:04 | 45504.7944 | 0.082167 | 0.00034236 | 22 | 5280 | Unplanned | Defective Equipment | Damaged conductor between pole 35312 & 35308
|  | O-1018-C | North River |  | Ruakaka CB7 | 2024-08-01 09:01 | 45505.3757 | 2024-08-01 13:40 | 45505.5694 | 0.36446 | 0.0013063 | 84 | 23436 | Planned | Planned Interruption | Replace HV & LV cross arms, guy wires and connections at various sites
|  | O-1027-C | Thelma Road |  | Mangawhai North CB4 | 2024-08-01 09:58 | 45505.4153 | 2024-08-01 14:42 | 45505.6125 | 0.0044166 | 1.5551e-05 | 1 | 284 | Planned | Planned Interruption | Network Maintenance - Replace crossarms and hardware at pole 29746 to EOL
|  | O-4492-B | Mata |  | Ruakaka CB3 | 2024-08-02 09:08 | 45506.3806 | 2024-08-02 11:40 | 45506.4861 | 0.03073 | 0.00020217 | 13 | 1976 | Planned | Planned Interruption | Replacing 11kv 400v poles & Cross arms and TX RO218
|  | O-4501-B | Hokianga Rd |  | Dargaville CB7 | 2024-08-02 09:18 | 45506.3875 | 2024-08-02 12:38 | 45506.5264 | 0.42474 | 0.0022239 | 143 | 27312 | Planned | Planned Interruption | Remove pole #53535, cut LV over on to new Tx DA44, liven new Tx DA44
|  | F-6841-A | Paparoa |  | Mareretu CB6 | 2024-08-02 22:44 | 45506.9472 | 2024-08-03 00:16 | 45507.0111 | 0.087275 | 0.00094864 | 61 | 5612 | Unplanned | Adverse Environment | FP 385091 - Isolated for safety - pole straighten & install temp guys
|  | F-6850-A | Marsden Bay |  | Bream Bay CB1107 | 2024-08-04 04:08 | 45508.1722 | 2024-08-04 04:37 | 45508.1924 | 0.011275 | 0.00038879 | 25 | 725 | Unplanned | Wildlife | FP385098 - Possum
|  | O-4495-B | Waipu |  | Ruakaka CB2 | 2024-08-05 09:02 | 45509.3762 | 2024-08-05 14:46 | 45509.6151 | 1.0539 | 0.0030636 | 197 | 67771 | Planned | Planned Interruption | Network Maintenance replace cross arms connections and ampacts
|  | O-1042-C | Langs Beach |  | Mangawhai North CB3 | 2024-08-05 09:12 | 45509.3833 | 2024-08-05 09:45 | 45509.4062 | 0.039003 | 0.0011819 | 76 | 2508 | Planned | Planned Interruption | Replace pole 10598 and HV cable riser/crucifix
|  | F-6859-A | Puwera |  | Maungatapere CB7 | 2024-08-05 14:57 | 45509.6229 | 2024-08-05 15:34 | 45509.6486 | 0.072501 | 0.0019595 | 126 | 4662 | Unplanned | Defective Equipment | 385129 / Isolate HV to repair spragged wires between poles 46094 & 46095
|  | O-892-C | Montgomery Ave |  | Onerahi CB8 | 2024-08-06 09:01 | 45510.376 | 2024-08-06 15:10 | 45510.6321 | 0.41874 | 0.0011353 | 73 | 26926 | Planned | Planned Interruption | 11kV Pole & Hardware replacements
|  | O-4648-B | Maunu Road |  | Whangarei South CB1102 | 2024-08-07 09:04 | 45511.3778 | 2024-08-07 15:13 | 45511.634 | 1.0846 | 0.0029392 | 189 | 69741 | Planned | Planned Interruption | HV/LV ARM & HARDWARE REPLACEMENT
|  | O-4504-B | Thelma Road |  | Mangawhai North CB4 | 2024-08-08 09:04 | 45512.3778 | 2024-08-08 11:52 | 45512.4944 | 0.14108 | 0.00083978 | 54 | 9072 | Planned | Planned Interruption | Network Maintenance - straighten pole, redo HV & LV connections and remove redundant LV pole
|  | O-4507-B | Puwera |  | Maungatapere CB7 | 2024-08-08 09:10 | 45512.3819 | 2024-08-08 12:43 | 45512.5299 | 0.41737 | 0.0019595 | 126 | 26838 | Planned | Planned Interruption | Network Maintenance - Essential 11kv works
|  | F-6883-A | Puwera |  | Maungatapere CB7 | 2024-08-08 16:41 | 45512.6951 | 2024-08-09 11:34 | 45513.4819 | 0.01762 | 1.5551e-05 | 1 | 1133 | Unplanned | Defective Equipment | FP385228 - replaced faulty Tx X200
|  | O-4561-B | North River |  | Ruakaka CB7 | 2024-08-09 09:04 | 45513.3778 | 2024-08-09 13:53 | 45513.5785 | 0.87191 | 0.003017 | 194 | 56066 | Planned | Planned Interruption | Replace cross arms and fuses, remove redundant hardware
|  | O-4486-B | Langs Beach |  | Mangawhai North CB3 | 2024-08-09 09:07 | 45513.3799 | 2024-08-09 12:18 | 45513.5125 | 0.017822 | 9.3309e-05 | 6 | 1146 | Planned | Planned Interruption | Isolate & earth works area for safety and tidy up work. Remove conductors 400m span over bush area with Skyworks Helicopter
|  | O-4360-B | Tikipunga Hill |  | Tikipunga CB4 | 2024-08-09 09:28 | 45513.3944 | 2024-08-09 15:51 | 45513.6604 | 0.27994 | 0.00073092 | 47 | 18001 | Planned | Planned Interruption | Replace concrete base and 11kv cable riser.
|  | O-1030-C | Thelma Road |  | Mangawhai North CB4 | 2024-08-09 09:51 | 45513.4104 | 2024-08-09 14:32 | 45513.6056 | 0.14858 | 0.00052875 | 34 | 9554 | Planned | Planned Interruption | Install new Tx MC 582
|  | F-6880-A | Tangaihi |  | Ruawai CB1032 | 2024-08-09 10:38 | 45513.4431 | 2024-08-09 12:32 | 45513.5222 | 0.16842 | 0.0014774 | 95 | 10830 | Unplanned | Defective Equipment | Urgent shut (not notified) to replace Xarm pole 28865
|  | F-6892-A | Marsden Bay |  | Bream Bay CB1107 | 2024-08-10 09:10 | 45514.3819 | 2024-08-10 11:16 | 45514.4694 | 1.6808 | 0.025536 | 1642 | 108078 | Unplanned | Unknown | 385272/ Unknown - Trip O/C Phase BC. Patrolled & Livened in sections. Relay data downloaded.
|  | F-6901-A | Te Kopuru |  | Dargaville CB2 | 2024-08-11 05:57 | 45515.2479 | 2024-08-11 06:13 | 45515.2588 | 0.19766 | 0.014681 | 944 | 12710 | Unplanned | Unknown | Overcurrent Trip A & C. Successful 15 minute close on CB 2 DAR.
|  | F-6868-A | North Dargaville |  | Dargaville CB1 | 2024-08-12 09:36 | 45516.4 | 2024-08-12 16:23 | 45516.6826 | 0.018553 | 4.6654e-05 | 3 | 1193 | Unplanned | Defective Equipment | Pole replacement and line lift @ Pole 25813
|  | O-1051-C | Hakaru |  | Kaiwaka CB1032 | 2024-08-12 10:01 | 45516.4174 | 2024-08-12 14:25 | 45516.6007 | 0.2915 | 0.0011042 | 71 | 18744 | Planned | Planned Interruption | LV maintenance to replace Xarms, connections and pillars past L425
|  | F-6904-A | Te Kopuru |  | Dargaville CB2 | 2024-08-12 11:06 | 45516.4625 | 2024-08-12 11:58 | 45516.4985 | 0.074912 | 0.0014463 | 93 | 4817 | Unplanned | Defective Equipment | 385290. Isolate to repair blown jumper at pole 301791
|  | F-6910-A | Kaiatea |  | Ngunguru CB1072 | 2024-08-12 14:56 | 45516.6222 | 2024-08-12 15:12 | 45516.6331 | 0.071164 | 0.010606 | 682 | 4576 | Unplanned | Unknown | Trip & 15 Min Close on Sw 720. FPIs at Sw 720 Activated.
|  | O-4564-B | Waipu |  | Ruakaka CB2 | 2024-08-14 09:03 | 45518.3768 | 2024-08-14 13:37 | 45518.5676 | 0.70941 | 0.0025815 | 166 | 45617 | Planned | Planned Interruption | Network Maintenance replacing poles cross arms and connections
|  | O-4477-B | Tangowahine |  | Dargaville CB8 | 2024-08-14 10:16 | 45518.4278 | 2024-08-14 11:31 | 45518.4799 | 0.017495 | 0.00023327 | 15 | 1125 | Planned | Planned Interruption | Replace Stud pole underneath 11kV line and re instate guy wire
|  | F-6922-A | Maungakaramea |  | Maungatapere CB3 | 2024-08-15 09:52 | 45519.4111 | 2024-08-15 12:07 | 45519.5049 | 0.13436 | 0.0009953 | 64 | 8640 | Unplanned | Defective Equipment | FP385390 Repair spragged line/dead end & change rotten cross-arm
|  | F-6925-A | Ararua |  | Mareretu CB2 | 2024-08-15 10:31 | 45519.4382 | 2024-08-15 13:38 | 45519.5681 | 0.00094864 | 3.1103e-05 | 2 | 61 | Unplanned | Defective Equipment | Transformer replacement E283 due to siezed tapchanger
|  | F-6943-A | Charles St |  | Kamo CB2 | 2024-08-15 13:41 | 45519.5702 | 2024-08-16 20:16 | 45520.8444 | 0.028537 | 1.5551e-05 | 1 | 1835 | Unplanned | Defective Equipment | FP385405 UG HV Cable fault
|  | F-6955-A | Te Kopuru |  | Dargaville CB2 | 2024-08-17 22:07 | 45521.9219 | 2024-08-18 03:14 | 45522.1344 | 1.0732 | 0.021834 | 1404 | 69010 | Unplanned | Third Party Interference | FP385454 Car Vs Pole 14046 - Event # F4031845
|  | F-6958-A | Te Kopuru |  | Dargaville CB2 | 2024-08-18 04:20 | 45522.1803 | 2024-08-18 04:35 | 45522.1907 | 0.13127 | 0.014681 | 944 | 8441 | Unplanned | Vegetation | Tripped & closed after 15mins - Sw 2255 FPI's activated - Unknown cause, later found line down on F-6979-A caused by rotten tree
|  | F-6973-A | North Dargaville |  | Dargaville CB1 | 2024-08-18 08:32 | 45522.3558 | 2024-08-19 11:36 | 45523.4833 | 0.11995 | 0.00038879 | 25 | 7713 | Unplanned | Unknown | FP 385455 - Replace Transformer but no cause found
|  | F-6970-A | Te Kopuru |  | Dargaville CB2 | 2024-08-18 11:46 | 45522.4903 | 2024-08-18 12:57 | 45522.5396 | 0.80656 | 0.014681 | 944 | 51864 | Unplanned | Vegetation | FP 385463 - Trip OC Phase AC patrolled nothing found. Later found line down on F-6979-A caused by rotten tree fell on line
|  | F-6967-A | Coast |  | Dargaville CB6 | 2024-08-18 12:00 | 45522.5 | 2024-08-18 19:53 | 45522.8287 | 0.36009 | 0.001353 | 87 | 23155 | Unplanned | Defective Equipment | FP 385462 / F 4032091 - Reported pole on fire. Replaced DDOs & LV xarm.
|  | F-6979-A | Te Kopuru |  | Dargaville CB2 | 2024-08-18 16:11 | 45522.6743 | 2024-08-19 01:28 | 45523.0614 | 1.9814 | 0.036142 | 3244 | 128293 | Unplanned | Vegetation | FP 385472 - Lines Down between Poles 14287 & Pole 14286 caused by rotten tree fell on line
|  | F-6985-A | Tangaihi |  | Ruawai CB1032 | 2024-08-18 17:36 | 45522.7333 | 2024-08-18 18:33 | 45522.7729 | 0.070915 | 0.0012441 | 80 | 4560 | Unplanned | Defective Equipment | FP 385468 - Repair jumper load side of Links 3076
|  | F-7003-A | Paranui |  | Tikipunga CB6 | 2024-08-19 15:04 | 45523.6278 | 2024-08-19 19:52 | 45523.8278 | 0.64386 | 0.017604 | 1132 | 41402 | Unplanned | Vegetation | FP 385527 - Removed tree from lines
|  | F-7009-A | Waipu |  | Ruakaka CB2 | 2024-08-20 07:17 | 45524.3035 | 2024-08-20 07:32 | 45524.3141 | 0.071226 | 0.015474 | 995 | 4580 | Unplanned | Unknown | Trip EF A & N. FPIUs Sw 545 activated. 15 Min Close on Swq 545 & BTN
|  | F-7012-A | Waipu |  | Ruakaka CB2 | 2024-08-20 08:30 | 45524.3542 | 2024-08-20 10:52 | 45524.4528 | 0.43879 | 0.015474 | 995 | 28215 | Unplanned | Unknown | Second trip of day. Trip EF A & N. Fault between Sw 545 & 5434. Patrolled & nothing found. Closed & BTN. Switching on F-7015-A
|  | O-14920-A | Ararua |  | Mareretu CB2 | 2024-08-20 09:12 | 45524.3833 | 2024-08-20 13:58 | 45524.5819 | 0.11119 | 0.00038879 | 25 | 7150 | Planned | Planned Interruption | Replacement of LV X-Arms & reconductoring works below 11kV circuit
|  | O-15004-A | Thelma Road |  | Mangawhai North CB4 | 2024-08-20 09:23 | 45524.391 | 2024-08-20 13:47 | 45524.5743 | 0.50499 | 0.0019128 | 123 | 32472 | Planned | Planned Interruption | Remove bonded earth from crucifix at pole 312091, remove temp break at pole 3120 VLF test cable between SW4184 and pole 312091
|  | F-7018-A | Ararua |  | Mareretu CB2 | 2024-08-20 13:23 | 45524.5576 | 2024-08-20 16:29 | 45524.6868 | 0.020995 | 0.00012441 | 8 | 1350 | Unplanned | Defective Equipment | 385539 / Isolate via Temp Break at pole 48406 & Straighten poles and re sag low 11kV lines.
|  | O-4612-B | Hokianga Rd |  | Dargaville CB7 | 2024-08-21 08:15 | 45525.3434 | 2024-08-21 14:14 | 45525.5931 | 0.011182 | 3.1103e-05 | 2 | 719 | Planned | Planned Interruption | Safe Transport of a High Load. House being maneuvered around lines.
|  | O-15007-A | Te Kopuru |  | Dargaville CB2 | 2024-08-21 09:39 | 45525.4022 | 2024-08-21 13:35 | 45525.5663 | 0.20942 | 0.00088644 | 57 | 13466 | Planned | Planned Interruption | Replace Pole 13925
|  | F-7027-A | Bickerstaff |  | Maungaturoto CB2 | 2024-08-21 14:15 | 45525.5938 | 2024-08-21 14:47 | 45525.616 | 0.011446 | 0.00035768 | 23 | 736 | Unplanned | Defective Equipment | Replace binder - FP385600
|  | F-7030-A | Otonga |  | Hikurangi CB1032 | 2024-08-21 18:46 | 45525.7818 | 2024-08-22 10:57 | 45526.4563 | 2.1227 | 0.02566 | 1650 | 136495 | Unplanned | Defective Equipment | FP 385612. HV line down @ pole 57409. Delays due to comms issues & difficulty operating Sw 6059.
|  | O-4552-B | Hatea Drive |  | Tikipunga CB3 | 2024-08-22 09:04 | 45526.3778 | 2024-08-22 16:06 | 45526.6708 | 0.48564 | 0.0011508 | 74 | 31228 | Planned | Planned Interruption | Installing New Transformer WC286.
|  | O-15073-A | Turiwiri |  | Dargaville CB9 | 2024-08-22 09:10 | 45526.3819 | 2024-08-22 15:09 | 45526.6312 | 0.11724 | 0.00032658 | 21 | 7539 | Planned | Planned Interruption | Network Maintenance Replace Pole & Crossarms
|  | F-7045-A | Norfolk St |  | Alexander St CB1 | 2024-08-22 16:25 | 45526.684 | 2024-08-22 21:43 | 45526.9049 | 0.36596 | 0.0011508 | 74 | 23532 | Unplanned | Defective Equipment | FP 385655 Blown HV fuse @ RMU Sw162
|  | F-7048-A | Access Rd |  | Ruawai CB1022 | 2024-08-22 19:37 | 45526.8174 | 2024-08-22 19:58 | 45526.8319 | 0.00032658 | 1.5551e-05 | 1 | 21 | Unplanned | Unknown | 385660 / 1 x HV Fuse blown, Opened remaining fuse and reloaded, Closed. BTN No obvious cause.
|  | F-7054-A | Whangarei Heads |  | Parua Bay CB3 | 2024-08-23 11:54 | 45527.496 | 2024-08-23 12:09 | 45527.5065 | 0.081474 | 0.012379 | 796 | 5239 | Unplanned | Unknown | N/A Tripped A&B phase O/C - Unknown
|  | F-7057-A | Waipu |  | Ruakaka CB2 | 2024-08-24 03:37 | 45528.1507 | 2024-08-24 07:01 | 45528.2925 | 0.68078 | 0.024991 | 1607 | 43776 | Unplanned | Defective Equipment | 385693 / Faulty Jumper at Tx RR104
|  | O-4624-B | Titoki |  | Poroti CB1032 | 2024-08-26 10:24 | 45530.4333 | 2024-08-26 13:31 | 45530.5632 | 0.011633 | 6.2206e-05 | 4 | 748 | Planned | Planned Interruption | Refurbish Dsub P183 with the 11KV live overhead and straighten pole 50487
|  | F-7078-A | Ruatangata |  | Kamo CB6 | 2024-08-27 06:48 | 45531.2832 | 2024-08-27 11:40 | 45531.4861 | 0.94247 | 0.011586 | 745 | 60603 | Unplanned | Third Party Interference | FENZ F4037448 / FP 385745 - Car Vs Pole - Replaced pole
|  | O-4015-B | Austin Road |  | Maunu CB1072 | 2024-08-27 09:05 | 45531.3785 | 2024-08-27 18:55 | 45531.7882 | 0.57805 | 0.00097974 | 63 | 37170 | Planned | Planned Interruption | Replace SW/7746/7747/7748. Complete joints on existing H/V cables to connect to new switch.
|  | O-4549-B | Hatea Drive |  | Tikipunga CB3 | 2024-08-27 09:08 | 45531.3806 | 2024-08-27 15:05 | 45531.6285 | 0.43541 | 0.0012286 | 79 | 27998 | Planned | Planned Interruption | Removing TX WC 246, Installing New TX WC283
|  | O-4633-B | Access Rd |  | Ruawai CB1022 | 2024-08-28 09:04 | 45532.3778 | 2024-08-28 14:13 | 45532.5924 | 0.51418 | 0.001664 | 107 | 33063 | Planned | Planned Interruption | Replace Xarms and hardware & Redo HV connections
|  | O-15010-A | Langs Beach |  | Mangawhai North CB3 | 2024-08-28 09:41 | 45532.4035 | 2024-08-28 15:14 | 45532.6347 | 0.39358 | 0.0011819 | 76 | 25308 | Planned | Planned Interruption | Replace pole 10598 and HV cable riser/crucifix
|  | F-7081-A | Access Rd |  | Ruawai CB1022 | 2024-08-28 10:22 | 45532.432 | 2024-08-28 10:38 | 45532.4433 | 0.08205 | 0.012068 | 776 | 5276 | Unplanned | Unknown | FPIs at switches 2077 and 2156 activated. Note: Sw2077 was Closed & Sw2235 Open due to a planned outage.
|  | F-7084-A | Marsden Bay |  | Bream Bay CB1107 | 2024-08-28 14:20 | 45532.5972 | 2024-08-29 03:51 | 45533.1605 | 4.1929 | 0.065425 | 4207 | 269612 | Unplanned | Third Party Interference | F4038585 / FP 385804 - Car Vs Pole 13404 & Repair Crucifix at Pole 408734
|  | O-4627-B | North River |  | Ruakaka CB7 | 2024-08-29 09:01 | 45533.3758 | 2024-08-29 14:14 | 45533.5932 | 0.46258 | 0.0014774 | 95 | 29745 | Planned | Planned Interruption | Replace poles 40994 and 40979, HV fuses and LA's at Dsub RB169 and HV and LV cross arms at various sites.
|  | O-4600-B | King Road |  | Mangawhai North CB2 | 2024-08-29 09:04 | 45533.3778 | 2024-08-29 14:41 | 45533.6118 | 0.020963 | 6.2206e-05 | 4 | 1348 | Planned | Planned Interruption | Replace Tx like for like
|  | O-4597-B | Maunu Road |  | Whangarei South CB1102 | 2024-08-29 09:07 | 45533.3799 | 2024-08-29 14:46 | 45533.6153 | 0.31632 | 0.00093309 | 60 | 20340 | Planned | Planned Interruption | Network Extension upgrade Tx from 200kVA to a 300kVA
|  | F-7093-A | Hakaru |  | Kaiwaka CB1032 | 2024-08-29 15:14 | 45533.6347 | 2024-08-29 15:29 | 45533.6453 | 0.19726 | 0.012892 | 829 | 12684 | Unplanned | Lightning | Tripped on earth fault, no reports called though after 15 min. Closed - BTN
|  | F-7105-A | Dunns Rd |  | Ruawai CB1082 | 2024-08-29 15:30 | 45533.6458 | 2024-08-29 17:21 | 45533.7229 | 0.0034524 | 3.1103e-05 | 2 | 222 | Unplanned | Lightning | 385845 / 3 x HV fuses blown
|  | F-7111-A | Fert. Works |  | Kioreroa CB6 | 2024-08-29 18:18 | 45533.7626 | 2024-08-29 23:32 | 45533.9806 | 0.24366 | 0.0017262 | 111 | 15668 | Unplanned | Wildlife | FP 385851 - Sectionlised restoration, found lines down due to duck striking line.
|  | O-14935-A | Taipuha |  | Mareretu CB1 | 2024-08-30 09:00 | 45534.375 | 2024-08-30 12:34 | 45534.5236 | 0.14976 | 0.00069982 | 45 | 9630 | Planned | Planned Interruption | Network Maintenance replace cross arms and connections
|  | O-14926-A | Ararua |  | Mareretu CB2 | 2024-08-30 09:11 | 45534.3826 | 2024-08-30 14:25 | 45534.6007 | 0.12208 | 0.00038879 | 25 | 7850 | Planned | Planned Interruption | LV reconductoring works below 11kV circuit
|  | F-7126-A | Ararua |  | Mareretu CB2 | 2024-08-30 11:23 | 45534.4743 | 2024-08-30 13:38 | 45534.5681 | 0.016796 | 0.00012441 | 8 | 1080 | Unplanned | Defective Equipment | FP 385841 Low HV lines Btwn poles 48449 & 48450
|  | F-7147-A | Te Kopuru |  | Dargaville CB2 | 2024-08-31 12:13 | 45535.5087 | 2024-08-31 17:09 | 45535.7146 | 0.62725 | 0.014665 | 943 | 40334 | Unplanned | Third Party Interference | FP385885 Car Vs pole 14472 - Event number F4040278
|  | F-7150-A | Hakaru |  | Kaiwaka CB1032 | 2024-08-31 18:06 | 45535.7542 | 2024-08-31 18:57 | 45535.7896 | 0.034104 | 0.00066871 | 43 | 2193 | Unplanned | Lightning | FP 385887 1x HV fuse blown - Unknown (possible lightning). Replaced Fuse barrell.
|  | F-7159-A | Tangaihi |  | Ruawai CB1032 | 2024-09-01 01:43 | 45536.0715 | 2024-09-01 23:49 | 45536.9924 | 1.9399 | 0.031732 | 2041 | 124770 | Unplanned | Lightning | FP385896 - Tx K325 replaced - Lightning K324 blown fuse links barrell still stuck in. faulty lightning arrestor K312
|  | F-7168-A | Wairere |  | Mareretu CB5 | 2024-09-01 02:02 | 45536.0847 | 2024-09-01 02:19 | 45536.0967 | 0.071985 | 0.0064989 | 418 | 4630 | Unplanned | Lightning | Trip EF - FPIs Sw 381 N & C.
|  | F-7183-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-01 02:26 | 45536.1014 | 2024-09-01 02:48 | 45536.1166 | 0.245 | 0.012065 | 776 | 15758 | Unplanned | Lightning | EF Trip. Multplie reported of DDOs open on this feeder.
|  | F-7234-A | Wairere |  | Mareretu CB5 | 2024-09-01 05:05 | 45536.2118 | 2024-09-01 08:19 | 45536.3465 | 0.033178 | 0.00017102 | 11 | 2134 | Unplanned | Lightning | FP - 385900 - Reloaded and closed HV Fuses
|  | F-7204-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-01 05:44 | 45536.2389 | 2024-09-01 06:26 | 45536.2681 | 0.0045554 | 0.00010883 | 7 | 293 | Unplanned | Lightning | FP 385902 - Reload and closed HV Fuses
|  | F-7261-A | Access Rd |  | Ruawai CB1022 | 2024-09-01 05:56 | 45536.247 | 2024-09-01 10:48 | 45536.45 | 0.031826 | 0.00010883 | 7 | 2047 | Unplanned | Lightning | FP 385904 - 3x blown HV Fuses E384. Reloaded and Closed.
|  | F-7228-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-01 08:07 | 45536.3382 | 2024-09-01 10:49 | 45536.4507 | 0.0050374 | 3.1095e-05 | 2 | 324 | Unplanned | Lightning | FP385922 - Repair jumper D178
|  | F-7276-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-01 08:29 | 45536.3531 | 2024-09-01 11:55 | 45536.4965 | 0.012842 | 6.219e-05 | 4 | 826 | Unplanned | Lightning | FP 385926 - Reload and close HV Fuses.
|  | F-7243-A | Dunns Rd |  | Ruawai CB1082 | 2024-09-01 08:58 | 45536.3739 | 2024-09-01 09:19 | 45536.3882 | 0.063854 | 0.0057059 | 367 | 4107 | Unplanned | Unknown | CB 1082 EF trip. FPIs Sw 2049 EF.
|  | F-7297-A | Access Rd |  | Ruawai CB1022 | 2024-09-01 10:48 | 45536.4499 | 2024-09-01 13:29 | 45536.5618 | 0.015034 | 9.3285e-05 | 6 | 967 | Unplanned | Lightning | FP385944 - 3x HV fuses blown F104
|  | F-7279-A | Ararua |  | Mareretu CB2 | 2024-09-01 12:04 | 45536.5028 | 2024-09-01 12:43 | 45536.5299 | 0.0048508 | 0.00012438 | 8 | 312 | Unplanned | Lightning | FP 385901-HV fuse replaced E221, found also L3060 blown x1
|  | F-7306-A | Kaiwaka South |  | Kaiwaka CB1072 | 2024-09-01 18:59 | 45536.791 | 2024-09-01 19:14 | 45536.8017 | 0.12394 | 0.0080225 | 516 | 7972 | Unplanned | Unknown | Tripped O/C - Unknown Sw 320 B&C phase activated
|  | F-7312-A | Tangaihi |  | Ruawai CB1032 | 2024-09-02 09:06 | 45537.3794 | 2024-09-02 12:01 | 45537.5007 | 0.0081469 | 4.6643e-05 | 3 | 524 | Unplanned | Lightning | FP 385969 - 3x blown HV fuses tx K316
|  | O-4657-B | Tikipunga Hill |  | Tikipunga CB4 | 2024-09-02 09:11 | 45537.3826 | 2024-09-02 15:17 | 45537.6368 | 0.22193 | 0.00060635 | 39 | 14274 | Planned | Planned Interruption | Replace 150kva Tx TT125 with a 300kva. Replace concrete pad as well.
|  | O-4537-B | North River |  | Ruakaka CB7 | 2024-09-03 09:03 | 45538.3769 | 2024-09-03 13:24 | 45538.5585 | 0.38634 | 0.001477 | 95 | 24849 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-15121-A | Brynderwyn |  | Maungaturoto CB1 | 2024-09-03 09:12 | 45538.3833 | 2024-09-03 13:36 | 45538.5667 | 0.016418 | 6.219e-05 | 4 | 1056 | Planned | Planned Interruption | Network Maintenance - At pole 49851 Redo HV connections, Repair HV pole backstay, Re-sag LV conductors
|  | F-7336-A | Waipu |  | Ruakaka CB2 | 2024-09-03 11:50 | 45538.4927 | 2024-09-03 16:51 | 45538.7021 | 0.41989 | 0.02881 | 1853 | 27007 | Unplanned | Vegetation | FP 360038 - Lines down between poles 10383 & 10384
|  | O-14941-A | Taipuha |  | Mareretu CB1 | 2024-09-04 09:01 | 45539.3756 | 2024-09-04 14:39 | 45539.6101 | 0.38853 | 0.0011505 | 74 | 24990 | Planned | Planned Interruption | Network Maintenance replace cross arms and connections
|  | O-15106-A | Marsden Pt |  | Ruakaka CB1 | 2024-09-04 09:05 | 45539.3785 | 2024-09-04 14:17 | 45539.5951 | 0.14552 | 0.00046643 | 30 | 9360 | Planned | Planned Interruption | Replacing 11kv 400v poles & cross arms and LV conductor.
|  | F-7348-A | North River |  | Ruakaka CB7 | 2024-09-04 18:19 | 45539.7632 | 2024-09-04 19:47 | 45539.8243 | 0.15734 | 0.001788 | 115 | 10120 | Unplanned | Defective Equipment | FP 386078 - Low Lines - replaced pole to correct height
|  | O-4540-B | North River |  | Ruakaka CB7 | 2024-09-05 09:08 | 45540.3807 | 2024-09-05 14:12 | 45540.5914 | 0.44817 | 0.001477 | 95 | 28826 | Planned | Planned Interruption | Replace HV & LV cross arms
|  | O-15049-A | Fraser |  | Kioreroa CB5 | 2024-09-05 21:44 | 45540.9055 | 2024-09-05 22:57 | 45540.9565 | 0.08803 | 0.0011972 | 77 | 5662 | Planned | Planned Interruption | High load transport from 211 Port Road, Whangarei to 245 Port Road, Whangarei
|  | O-15001-A | North River |  | Ruakaka CB7 | 2024-09-06 09:09 | 45541.3812 | 2024-09-06 14:34 | 45541.6069 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Remove/decommission pole mount Tx RB232. Replace 11kv arm and fit new fuses at pole 39107. Connect and liven new ground mount 20
|  | O-15130-A | Maungakaramea |  | Maungatapere CB3 | 2024-09-06 09:31 | 45541.3965 | 2024-09-06 13:26 | 45541.5597 | 0.025576 | 0.00010883 | 7 | 1645 | Planned | Planned Interruption | Network Extension upgrade transformer and and hardware as per 1c plan
|  | O-14998-A | Turiwiri |  | Dargaville CB9 | 2024-09-06 09:39 | 45541.4021 | 2024-09-06 15:03 | 45541.6271 | 0.2015 | 0.0006219 | 40 | 12960 | Planned | Planned Interruption | Cut Trees around 11kv lines
|  | F-7354-A | Titoki |  | Poroti CB1032 | 2024-09-06 18:12 | 45541.7583 | 2024-09-06 18:28 | 45541.7694 | 0.14971 | 0.011972 | 770 | 9629 | Unplanned | Unknown | Trip OC BC, High fault current measured on POR CB 3022 so left for 15min attempt close - Unknown. No FPI indication
|  | F-7360-A | Tangaihi |  | Ruawai CB1032 | 2024-09-07 14:00 | 45542.5835 | 2024-09-07 17:08 | 45542.714 | 0.18248 | 0.004913 | 316 | 11737 | Unplanned | Defective Equipment | 386175 - Rusted Kingbolt, twisted crossarm. Replace Kingbolt and supporting bracket bolts
|  | F-7366-A | North Dargaville |  | Dargaville CB1 | 2024-09-08 08:39 | 45543.3604 | 2024-09-08 09:53 | 45543.4118 | 0.032214 | 0.00043533 | 28 | 2072 | Unplanned | Unknown | FP386179 - Blown Fuse L10099 - patrol line
|  | O-4660-B | Charles St |  | Kamo CB2 | 2024-09-08 09:02 | 45543.3764 | 2024-09-08 14:20 | 45543.5972 | 0.16316 | 0.00051307 | 33 | 10494 | Planned | Planned Interruption | Remove/decommission existing transformer KR130. Replace pole 54212 with B11. Fit new 11kv fuses and crucifix and connect and l
|  | O-4570-B | Whau Valley |  | Tikipunga CB1 | 2024-09-09 09:16 | 45544.3861 | 2024-09-09 17:41 | 45544.7368 | 0.5025 | 0.00099504 | 64 | 32320 | Planned | Planned Interruption | Stage 1 Installation of new RMU 10130, 10131, 10132 & 10133.
|  | O-4579-B | Whau Valley |  | Tikipunga CB1 | 2024-09-10 09:05 | 45545.3785 | 2024-09-10 15:13 | 45545.634 | 0.56375 | 0.0015548 | 100 | 36260 | Planned | Planned Interruption | Stage 2 Connect Sw 10133 to Tx KK124, connect Sw 10131 to Tx KK125
|  | O-15172-A | Tangaihi |  | Ruawai CB1032 | 2024-09-10 09:13 | 45545.384 | 2024-09-10 13:37 | 45545.5674 | 0.17239 | 0.000653 | 42 | 11088 | Planned | Planned Interruption | Replace Poles & Crossarms
|  | O-15370-A | North River |  | Ruakaka CB7 | 2024-09-10 09:32 | 45545.3971 | 2024-09-10 11:25 | 45545.476 | 0.40599 | 0.0035759 | 230 | 26113 | Planned | Planned Interruption | Replace defective cross arm on pole 39150
|  | O-4573-B | Whau Valley |  | Tikipunga CB1 | 2024-09-11 09:14 | 45546.3847 | 2024-09-11 18:02 | 45546.7514 | 0.27911 | 0.00052862 | 34 | 17952 | Planned | Planned Interruption | Remove 11KV cable from Sw7358 (redundant RMU) connect to SW 10130. Network Switching BTN
|  | O-15019-A | Langs Beach |  | Mangawhai North CB3 | 2024-09-11 09:32 | 45546.3972 | 2024-09-11 13:32 | 45546.5639 | 0.037314 | 0.00015548 | 10 | 2400 | Planned | Planned Interruption | P05D RMU servicing
|  | O-15148-A | Mangawhai Heads |  | Mangawhai North CB1 | 2024-09-11 09:38 | 45546.4014 | 2024-09-11 15:04 | 45546.6278 | 0.78055 | 0.0023943 | 154 | 50204 | Planned | Planned Interruption | Network Extension - Replace pole 906635. Install Temp SW on pole 14150 (closed position). Replace pole 14153.
|  | F-7402-A | Tangowahine |  | Dargaville CB8 | 2024-09-12 18:47 | 45547.7827 | 2024-09-12 19:03 | 45547.7936 | 0.046378 | 0.0089709 | 577 | 2983 | Unplanned | Unknown | Sw 2037 indicating fault
|  | O-15361-A | Tikipunga Hill |  | Tikipunga CB4 | 2024-09-13 09:01 | 45548.3757 | 2024-09-13 15:11 | 45548.6326 | 1.3759 | 0.0037314 | 240 | 88497 | Planned | Planned Interruption | Liven new safelink 10187/10188/10189/10190.
|  | F-7414-A | Three Mile Bush |  | Kamo CB3 | 2024-09-13 23:02 | 45548.9597 | 2024-09-14 01:00 | 45549.0417 | 0.21832 | 0.0018502 | 119 | 14042 | Unplanned | Defective Equipment | FP 386332 - Replace faulty insulator
|  | O-4681-B | Western Hills Dr |  | Alexander St CB7 | 2024-09-15 22:33 | 45550.9396 | 2024-09-16 02:12 | 45551.0917 | 0.010215 | 4.6643e-05 | 3 | 657 | Planned | Planned Interruption | Replacing Transformer WC282 & replacing pillar next to Burger King.
|  | F-7426-A | One Tree Point |  | Ruakaka CB6 | 2024-09-15 23:02 | 45550.9597 | 2024-09-16 04:08 | 45551.1722 | 0.27087 | 0.0028296 | 182 | 17422 | Unplanned | Defective Equipment | 386353 / Isolate to replace DDOs & Tx RO305 due to Oil leaking.
|  | F-7429-A | Brynderwyn |  | Maungaturoto CB1 | 2024-09-16 07:51 | 45551.3272 | 2024-09-16 10:34 | 45551.4403 | 0.17845 | 0.0029074 | 187 | 11478 | Unplanned | Third Party Interference | FP386359 Tractor clashed lines at quarry between poles 301379 & 300958 (damaged HV conductor)
|  | O-4672-B | ToeToe Rd |  | Kioreroa CB7 | 2024-09-16 09:03 | 45551.3771 | 2024-09-16 13:30 | 45551.5623 | 0.36066 | 0.0013526 | 87 | 23197 | Planned | Planned Interruption | ARM & HARDWARE REPLACEMENTS
|  | F-7405-A | Turiwiri |  | Dargaville CB9 | 2024-09-16 09:55 | 45551.4132 | 2024-09-16 11:26 | 45551.4764 | 0.0056593 | 6.219e-05 | 4 | 364 | Unplanned | Other Cause | FP386094 Install line break to cut away future redundant line & Tx's
|  | O-15721-A | Ararua |  | Mareretu CB2 | 2024-09-16 13:23 | 45551.5576 | 2024-09-16 14:37 | 45551.609 | 0.002301 | 3.1095e-05 | 2 | 148 | Unplanned | Defective Equipment | Broken binder found at Pole 48753 FP386372
|  | O-15187-A | Paranui |  | Tikipunga CB6 | 2024-09-17 09:03 | 45552.3774 | 2024-09-17 12:18 | 45552.5125 | 0.39312 | 0.0020212 | 130 | 25285 | Planned | Planned Interruption | Network Extension upgrade from 15kVA to 50kVA transformer
|  | O-4585-B | Onoke |  | Kamo CB8 | 2024-09-17 09:04 | 45552.3778 | 2024-09-17 10:25 | 45552.434 | 0.064227 | 0.00079292 | 51 | 4131 | Planned | Planned Interruption | Re configure Lightning arrrestors and lv fusing on transformer KV163
|  | O-15733-A | Taipuha |  | Mareretu CB1 | 2024-09-17 09:44 | 45552.4056 | 2024-09-17 09:46 | 45552.4069 | 6.219e-05 | 3.1095e-05 | 2 | 4 | Unplanned | Lightning | FP386406 1 x blown HV link - removed other two to inspect LV fuse boxes, reloaded blown HV link and closed in
|  | F-7447-A | Otonga |  | Hikurangi CB1032 | 2024-09-17 09:59 | 45552.4156 | 2024-09-17 10:40 | 45552.4446 | 0.38496 | 0.0092352 | 594 | 24760 | Unplanned | Defective Equipment | 386410 - LV Lines down outside 1146 Whananaki North Rd,Copper Iso HV for safety. LV Fail due to age.
|  | F-7450-A | 2nd Ave |  | Alexander St CB3 | 2024-09-17 12:34 | 45552.5236 | 2024-09-17 15:07 | 45552.6299 | 0.53989 | 0.0046176 | 297 | 34725 | Unplanned | Third Party Interference | FP386411 - Car v Pole
|  | F-7456-A | Access Rd |  | Ruawai CB1022 | 2024-09-17 14:44 | 45552.6139 | 2024-09-17 21:07 | 45552.8799 | 0.55654 | 0.0051773 | 333 | 35796 | Unplanned | Vegetation | FP386435 HV lines down due to tree falling between poles 338259 & 338425 - High winds
|  | F-7480-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-17 15:52 | 45552.6609 | 2024-09-17 18:35 | 45552.7743 | 0.0025342 | 1.5548e-05 | 1 | 163 | Unplanned | Lightning | FP386440 HV fuses blown - Lightning
|  | F-7510-A | Maungakaramea |  | Maungatapere CB3 | 2024-09-17 16:45 | 45552.6981 | 2024-09-17 20:27 | 45552.8521 | 0.027581 | 0.00012438 | 8 | 1774 | Unplanned | Lightning | FP 386450 Found HV fuses blown x2 @ Links 875 Intterruption time Ref F-7477-A
|  | F-7477-A | Maungakaramea |  | Maungatapere CB3 | 2024-09-17 16:45 | 45552.6981 | 2024-09-17 20:45 | 45552.8646 | 0.0074628 | 3.1095e-05 | 2 | 480 | Unplanned | Lightning | FP 386447 Lightning in area, Thought Tx was faulty but found Links 875 blown after earthing down Tx Ref F-7510-A
|  | F-7474-A | Bickerstaff |  | Maungaturoto CB2 | 2024-09-17 17:42 | 45552.7375 | 2024-09-17 17:48 | 45552.7417 | 0.00018657 | 3.1095e-05 | 2 | 12 | Unplanned | Lightning | FP386438 2x HV fuses blown - replaced back to normal
|  | F-7489-A | Paparoa |  | Mareretu CB6 | 2024-09-17 18:47 | 45552.7829 | 2024-09-17 19:04 | 45552.7946 | 0.15844 | 0.0094218 | 606 | 10191 | Unplanned | Lightning | Tripped O/C A&B phase - Lightning in the area
|  | F-7507-A | Mata |  | Ruakaka CB3 | 2024-09-18 00:30 | 45553.0208 | 2024-09-18 01:59 | 45553.0826 | 0.57701 | 0.0064833 | 417 | 37113 | Unplanned | Defective Equipment | FP386468 Blown HV jumper at pole 416735 towards pole 47073
|  | O-15103-A | Langs Beach |  | Mangawhai North CB3 | 2024-09-18 09:07 | 45553.3799 | 2024-09-18 14:51 | 45553.6188 | 0.12836 | 0.00037314 | 24 | 8256 | Planned | Planned Interruption | Upgrade conductor between pole 10705 and pole 10720
|  | F-7537-A | Whau Valley |  | Tikipunga CB1 | 2024-09-18 12:31 | 45553.5218 | 2024-09-18 16:37 | 45553.6924 | 1.9284 | 0.01987 | 1278 | 124032 | Unplanned | Third Party Interference | F4051510 / FP386506 - Car Vs Pole
|  | F-7555-A | Hakaru |  | Kaiwaka CB1032 | 2024-09-18 19:32 | 45553.8138 | 2024-09-18 23:29 | 45553.9783 | 0.71856 | 0.012904 | 830 | 46217 | Unplanned | Defective Equipment | FP386520 Binder broken and conductor come off onto Xarm at pole 45906
|  | F-7558-A | Whangarei Heads |  | Parua Bay CB3 | 2024-09-18 23:23 | 45553.9745 | 2024-09-18 23:38 | 45553.985 | 0.12794 | 0.012407 | 798 | 8229 | Unplanned | Unknown | O/C A&B phase - Unknown (F4)
|  | O-4687-B | ToeToe Rd |  | Kioreroa CB7 | 2024-09-19 09:02 | 45554.3766 | 2024-09-19 13:36 | 45554.5666 | 0.36583 | 0.0013371 | 86 | 23530 | Planned | Planned Interruption | ARM & HARDWARE REPLACEMENTS
|  | F-7570-A | North River |  | Ruakaka CB7 | 2024-09-19 22:31 | 45554.9384 | 2024-09-19 22:47 | 45554.9493 | 0.15645 | 0.017553 | 1129 | 10063 | Unplanned | Unknown | A B Phase OC. No FPIs on remote switches.
|  | F-7588-A | Tangowahine |  | Dargaville CB8 | 2024-09-21 05:51 | 45556.2434 | 2024-09-21 06:05 | 45556.2537 | 0.093985 | 0.0090331 | 581 | 6045 | Unplanned | Unknown | B & C Phase OC - No FPIs
|  | F-7597-A | Marsden Bay |  | Bream Bay CB1107 | 2024-09-21 15:30 | 45556.6458 | 2024-09-21 16:35 | 45556.691 | 0.51047 | 0.02556 | 1644 | 32833 | Unplanned | Unknown | 386610 / A B & C phase overcurrent. No fault found during patrol. All BTN
|  | F-7603-A | Springs Flat |  | Kamo CB1 | 2024-09-22 15:12 | 45557.6333 | 2024-09-22 15:26 | 45557.6433 | 0.20995 | 0.016076 | 1034 | 13504 | Unplanned | Unknown | Trip & 15 min close. A B & C Overcurrent
|  | O-15289-A | Tangowahine |  | Dargaville CB8 | 2024-09-23 09:12 | 45558.3833 | 2024-09-23 13:44 | 45558.5722 | 0.10572 | 0.00038869 | 25 | 6800 | Planned | Planned Interruption | Network Extension - Replace pole 324039 & liven 11kV up to links 10204 (Links to be left open)
|  | O-4666-B | Montgomery Ave |  | Onerahi CB8 | 2024-09-24 05:13 | 45559.2174 | 2024-09-24 06:48 | 45559.2833 | 0.12407 | 0.001306 | 84 | 7980 | Planned | Planned Interruption | Isolate 11KV so we can remove 11KV from stand offs on pole 300838. In preparation for switch replacement 285, 286, 287, 288.
|  | O-4621-B | Kokopu |  | Poroti CB1022 | 2024-09-24 09:02 | 45559.3764 | 2024-09-24 13:00 | 45559.5417 | 0.36633 | 0.0015392 | 99 | 23562 | Planned | Planned Interruption | HV & LV cross arm replacement, LV pole replacement and redo connections
|  | O-15637-A | Marsden Bay |  | Bream Bay CB1107 | 2024-09-24 09:03 | 45559.3771 | 2024-09-24 14:17 | 45559.5951 | 0.74693 | 0.0023788 | 153 | 48042 | Planned | Planned Interruption | Straighten double pole due to leaning towards the road (Rework) Re terminate LV terms Re position guy and remove LV connectors
|  | O-15385-A | King Road |  | Mangawhai North CB2 | 2024-09-24 09:04 | 45559.3781 | 2024-09-24 13:29 | 45559.5615 | 0.57918 | 0.0021922 | 141 | 37252 | Planned | Planned Interruption | Network Extension - Replace pole 32480 and install 3 phase 100KVA transformer labelled MC584
|  | O-15442-A | Brynderwyn |  | Maungaturoto CB1 | 2024-09-25 09:05 | 45560.3785 | 2024-09-25 15:26 | 45560.6431 | 0.27249 | 0.00071519 | 46 | 17526 | Planned | Planned Interruption | Network Maintenance - Replace HV & LV crossarms, straighten poles, redo HV connections.
|  | F-7633-A | Te Kopuru |  | Dargaville CB2 | 2024-09-26 08:36 | 45561.3585 | 2024-09-26 08:52 | 45561.3693 | 0.034858 | 0.0030473 | 196 | 2242 | Unplanned | Unknown | Relivened
|  | O-4684-B | Taipuha |  | Mareretu CB1 | 2024-09-26 09:02 | 45561.3765 | 2024-09-26 14:40 | 45561.6111 | 0.2654 | 0.00079292 | 51 | 17070 | Planned | Planned Interruption | Replace HV and LV poles and cross arms, Remove Tx B208
|  | O-15256-A | Titoki |  | Poroti CB1032 | 2024-09-27 09:03 | 45562.3771 | 2024-09-27 12:38 | 45562.5264 | 0.033427 | 0.00015548 | 10 | 2150 | Planned | Planned Interruption | Clear trees around 11kv from Pole 50186 to the end of line
|  | O-14977-A | Taipuha |  | Mareretu CB1 | 2024-09-27 09:06 | 45562.3792 | 2024-09-27 10:51 | 45562.4521 | 0.0016325 | 1.5548e-05 | 1 | 105 | Planned | Planned Interruption | Replace poles and crossarms
|  | O-15055-A | Whangarei Heads |  | Parua Bay CB3 | 2024-09-27 09:11 | 45562.3826 | 2024-09-27 15:04 | 45562.6278 | 0.38967 | 0.0011039 | 71 | 25063 | Planned | Planned Interruption | Replace pole 24431 with a B11. Remove and decommission existing Tx PO297. Connect new 11kv cable up pole and liven new Tx PO299
|  | O-15259-A | Titoki |  | Poroti CB1032 | 2024-09-27 09:34 | 45562.3986 | 2024-09-27 13:31 | 45562.5632 | 0.14739 | 0.0006219 | 40 | 9480 | Planned | Planned Interruption | Clear trees around network lines from pole Pole #50440 towards Pole #50426
|  | F-7642-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-09-27 13:03 | 45562.5439 | 2024-09-27 15:47 | 45562.6573 | 0.010153 | 6.219e-05 | 4 | 653 | Unplanned | Defective Equipment | 386790 - Repaired Xarm brace (nut off Xarm)
|  | F-7651-A | Tangaihi |  | Ruawai CB1032 | 2024-09-28 18:34 | 45563.7737 | 2024-09-28 22:49 | 45563.9507 | 0.18225 | 0.0024099 | 155 | 11722 | Unplanned | Defective Equipment | FP 386820 - Lines down in bull paddock. HV isolated remotely for safety. LV lines repaired.
|  | O-4630-B | Norfolk St |  | Alexander St CB1 | 2024-09-29 08:38 | 45564.3597 | 2024-09-29 15:50 | 45564.6597 | 0.15448 | 0.00035759 | 23 | 9936 | Planned | Planned Interruption | Replace Transformer WC231 & concrete foundation
|  | O-14971-A | Titoki |  | Poroti CB1032 | 2024-09-30 09:34 | 45565.3986 | 2024-09-30 10:50 | 45565.4514 | 0.040175 | 0.00052862 | 34 | 2584 | Planned | Planned Interruption | Clear trees around 11kv line from pole #346764
|  | O-15388-A | Ruawai Town |  | Ruawai CB1072 | 2024-10-01 09:08 | 45566.3806 | 2024-10-01 14:03 | 45566.5854 | 0.28416 | 0.00096325 | 62 | 18290 | Planned | Planned Interruption | replace poles, hardware and transformers like for like between pole 23342 to 23316
|  | O-4546-B | Waipu |  | Ruakaka CB2 | 2024-10-02 09:35 | 45567.3993 | 2024-10-02 11:41 | 45567.4868 | 0.12528 | 0.00099432 | 64 | 8064 | Planned | Planned Interruption | Straighten D/Sub RR279.
|  | O-15208-A | Wairere |  | Mareretu CB5 | 2024-10-02 09:37 | 45567.4007 | 2024-10-02 12:59 | 45567.541 | 0.3358 | 0.0016624 | 107 | 21614 | Planned | Planned Interruption | Straighten pole #28285 and replace 11kv cross arms, Retention 11kv from Pole #28284 to pole #28285 to gain height
|  | F-7663-A | Paparoa |  | Mareretu CB6 | 2024-10-02 20:57 | 45567.8729 | 2024-10-03 03:51 | 45568.1606 | 2.7819 | 0.018612 | 1198 | 179057 | Unplanned | Vegetation | 386935 / Trees on lines causing feeder to trip. Long outage time due to no MTO based staff & insufficent gear to carry out TB.
|  | O-15652-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-10-03 09:04 | 45568.3778 | 2024-10-03 12:46 | 45568.5319 | 0.27457 | 0.0012429 | 80 | 17673 | Planned | Planned Interruption | 33kV Height mitigation between poles 23157 and pole 23114
|  | O-15430-A | Whau Valley |  | Tikipunga CB1 | 2024-10-03 09:09 | 45568.3812 | 2024-10-03 14:59 | 45568.6243 | 0.0054377 | 1.5536e-05 | 1 | 350 | Planned | Planned Interruption | Replace ground mount D-sub WC109 with 500kva. Install new transformer base.
|  | O-15544-A | Fraser |  | Kioreroa CB5 | 2024-10-03 21:02 | 45568.8767 | 2024-10-03 23:25 | 45568.9755 | 0.17017 | 0.0011963 | 77 | 10953 | Planned | Planned Interruption | High load transport from 245 Port Road to 211 Port Road Whangarei
|  | O-15505-A | Pataua |  | Parua Bay CB1 | 2024-10-04 09:01 | 45569.3758 | 2024-10-04 13:59 | 45569.5825 | 0.47163 | 0.0015847 | 102 | 30357 | Planned | Planned Interruption | Remove L9825 Install new Tx OO561, L10214 & L10215
|  | O-15304-A | Bickerstaff |  | Maungaturoto CB2 | 2024-10-04 09:03 | 45569.3771 | 2024-10-04 13:30 | 45569.5625 | 0.23645 | 0.00088557 | 57 | 15219 | Planned | Planned Interruption | Remove TX D350 and install new pad mount TX and label D447
|  | O-15565-A | Walton St |  | Whangarei South CB1022 | 2024-10-04 09:10 | 45569.3819 | 2024-10-04 14:56 | 45569.6222 | 0.54218 | 0.0016002 | 103 | 34898 | Planned | Planned Interruption | Network Maintenance - LV ARM & HAREWARE REPLACEMENTS
|  | O-15283-A | Te Kopuru |  | Dargaville CB2 | 2024-10-04 10:01 | 45569.4176 | 2024-10-04 12:41 | 45569.5284 | 0.43898 | 0.0027499 | 177 | 28255 | Planned | Planned Interruption | Replace Sw 2153
|  | F-7678-A | North River |  | Ruakaka CB7 | 2024-10-05 08:49 | 45570.3676 | 2024-10-05 17:50 | 45570.7431 | 0.46676 | 0.0042103 | 271 | 30043 | Unplanned | Third Party Interference | 387007/ Recloser 1542 Trip EF Phase C to lockout. Vehicle hit OH Stay wire causing HV Line down & cracked pole
|  | O-4645-B | Hatea Drive |  | Tikipunga CB3 | 2024-10-06 08:36 | 45571.3583 | 2024-10-06 18:28 | 45571.7694 | 0.70821 | 0.0011963 | 77 | 45584 | Planned | Planned Interruption | Replace CFCF Switch 285-286-288-287. note cable fault between Sw 286 & WC248. ICP's livened WC248 via LV Bfeed from WC231
|  | F-7681-A | Jordan Valley |  | Hikurangi CB1102 | 2024-10-06 15:37 | 45571.6504 | 2024-10-06 22:09 | 45571.9229 | 0.4717 | 0.0073953 | 476 | 30361 | Unplanned | Defective Equipment | FP 387016 - lines down Rusk Rd
|  | O-4663-B | Montgomery Ave |  | Onerahi CB8 | 2024-10-07 05:47 | 45572.241 | 2024-10-07 06:43 | 45572.2799 | 0.073083 | 0.001305 | 84 | 4704 | Planned | Planned Interruption | Reconnect 11KV cables back onto stand off's at pole 300838.
|  | O-15478-A | Coast |  | Dargaville CB6 | 2024-10-07 09:12 | 45572.3833 | 2024-10-07 11:36 | 45572.4833 | 0.11186 | 0.00077681 | 50 | 7200 | Planned | Planned Interruption | Replace 11kv arms at pole #24926
|  | O-15592-A | Ararua |  | Mareretu CB2 | 2024-10-07 09:20 | 45572.3889 | 2024-10-07 12:58 | 45572.5403 | 0.094833 | 0.00043502 | 28 | 6104 | Planned | Planned Interruption | Replace 11kv cross arms at Pole #48550 and re tension 11kv lines to Pole #48554
|  | O-4555-B | Waipu |  | Ruakaka CB2 | 2024-10-07 09:42 | 45572.4042 | 2024-10-07 12:48 | 45572.5333 | 0.0057795 | 3.1073e-05 | 2 | 372 | Planned | Planned Interruption | High PD Investigate and clean 11KV cables.
|  | O-15622-A | Titoki |  | Poroti CB1032 | 2024-10-07 09:57 | 45572.4146 | 2024-10-07 13:26 | 45572.5596 | 0.42186 | 0.0020197 | 130 | 27153 | Planned | Planned Interruption | install new 50 kVA tx W545
|  | O-15364-A | Mangawhai Heads |  | Mangawhai North CB1 | 2024-10-08 09:05 | 45573.3786 | 2024-10-08 13:20 | 45573.5555 | 0.70059 | 0.0027499 | 177 | 45094 | Planned | Planned Interruption | Replace HV & LV crossarms and LV poles and earthing upgrade at MC252
|  | O-15328-A | Ruawai Town |  | Ruawai CB1072 | 2024-10-08 09:12 | 45573.3831 | 2024-10-08 15:16 | 45573.6358 | 0.30524 | 0.00083896 | 54 | 19647 | Planned | Planned Interruption | Network Maintenance - replace TX F207 like for like and hardware. Redo connections at pole 23312.
|  | F-7711-A | Treatment |  | Kioreroa CB2 | 2024-10-09 02:57 | 45574.1232 | 2024-10-09 05:08 | 45574.2139 | 0.41028 | 0.0034957 | 225 | 26408 | Unplanned | Unknown | 387103/ Trip O/C Phase BC. Patrolled & checked FPI's, Livened in sections.
|  | O-15556-A | Kokopu |  | Poroti CB1022 | 2024-10-09 09:01 | 45574.3757 | 2024-10-09 14:27 | 45574.6021 | 0.26844 | 0.00082342 | 53 | 17278 | Planned | Planned Interruption | Network Maintenance - POLE, ARM & HARDWARE REPLACEMENTS BETWEEN POLES 31434 & 31322
|  | O-15769-A | Kaiwaka South |  | Kaiwaka CB1072 | 2024-10-09 09:45 | 45574.4062 | 2024-10-09 15:22 | 45574.6403 | 0.30367 | 0.0009011 | 58 | 19546 | Planned | Planned Interruption | Upgrade Dsub C452 from 15 to 100kVA pole mount type. Replace 11kV strain insulators & other associated works.
|  | F-7720-A | Access Rd |  | Ruawai CB1022 | 2024-10-09 15:24 | 45574.6417 | 2024-10-09 15:50 | 45574.6597 | 0.0016158 | 6.2145e-05 | 4 | 104 | Unplanned | Unknown | FP387114 1 x HV Drop Out Fuse Blow with bad corrosion. Other Two dropped out for inspection
|  | O-15811-A | Union East |  | Kioreroa CB1 | 2024-10-10 05:39 | 45575.2354 | 2024-10-10 07:17 | 45575.3035 | 0.010658 | 0.00010875 | 7 | 686 | Planned | Planned Interruption | Maintenance on ZZ010
|  | O-15307-A | Ruawai Town |  | Ruawai CB1072 | 2024-10-10 09:10 | 45575.3819 | 2024-10-10 13:34 | 45575.5653 | 0.38555 | 0.0014604 | 94 | 24816 | Planned | Planned Interruption | Network Maintenance - Replace HV & LV crossarms
|  | O-16003-A | Kiripaka Rd |  | Tikipunga CB8 | 2024-10-10 09:12 | 45575.3833 | 2024-10-10 16:10 | 45575.6736 | 0.57798 | 0.0013827 | 89 | 37202 | Planned | Planned Interruption | Overlay existing 11kV underground cable due to storm water replacement
|  | O-15358-A | Kokopu |  | Poroti CB1022 | 2024-10-11 09:00 | 45576.375 | 2024-10-11 12:28 | 45576.5194 | 0.17127 | 0.00082342 | 53 | 11024 | Planned | Planned Interruption | CONDUCTOR, ARM & HARDWARE REPLACMENTS
|  | F-7732-A | Parua Bay |  | Parua Bay CB2 | 2024-10-12 01:11 | 45577.0493 | 2024-10-12 01:51 | 45577.0771 | 0.032937 | 0.00082342 | 53 | 2120 | Unplanned | Third Party Interference | FP387194 Reported car hit a run stay wire - found broken HV preform @ pole 30279
|  | F-7735-A | Tutukaka Block |  | Ngunguru CB1082 | 2024-10-12 13:52 | 45577.5781 | 2024-10-12 14:09 | 45577.5893 | 0.057795 | 0.010254 | 660 | 3720 | Unplanned | Unknown | Sw 7170 indicating Ph A&B. Successfully livened remotely.
|  | F-7738-A | Te Kopuru |  | Dargaville CB2 | 2024-10-13 07:32 | 45578.3138 | 2024-10-13 07:48 | 45578.3252 | 0.20499 | 0.014697 | 946 | 13194 | Unplanned | Unknown | Trip O/C Phase BC - Unknown. (Feeder Classification F4) 15min successful close
|  | O-15481-A | Tangowahine |  | Dargaville CB8 | 2024-10-14 09:36 | 45579.4 | 2024-10-14 10:57 | 45579.4563 | 0.069214 | 0.0008545 | 55 | 4455 | Planned | Planned Interruption | Replace 11kv Arms and connections at pole #37079
|  | O-15631-A | North River |  | Ruakaka CB7 | 2024-10-15 09:01 | 45580.3757 | 2024-10-15 14:14 | 45580.5931 | 0.55923 | 0.0017867 | 115 | 35995 | Planned | Planned Interruption | Pole, arm and hardware replacements
|  | O-15220-A | Ruawai Town |  | Ruawai CB1072 | 2024-10-15 09:06 | 45580.3792 | 2024-10-15 14:15 | 45580.5938 | 0.26404 | 0.0008545 | 55 | 16995 | Planned | Planned Interruption | Network Maintenance - replace TX F203 like for like and pole hardware. Replace LV crossarms - LV supplied from F204
|  | O-15013-A | Mangawhai Heads |  | Mangawhai North CB1 | 2024-10-15 09:39 | 45580.4021 | 2024-10-15 14:24 | 45580.6 | 1.0538 | 0.0036976 | 238 | 67830 | Planned | Planned Interruption | P05D RMU service
|  | F-7747-A | Access Rd |  | Ruawai CB1022 | 2024-10-15 17:54 | 45580.7458 | 2024-10-15 19:16 | 45580.8028 | 0.01274 | 0.00015536 | 10 | 820 | Unplanned | Defective Equipment | FP 387184 - Replaced 11kV Fuses E313
|  | O-976-C | Ararua |  | Mareretu CB2 | 2024-10-16 09:21 | 45581.3896 | 2024-10-16 14:40 | 45581.6111 | 0.2559 | 0.00080789 | 52 | 16471 | Planned | Planned Interruption | Network Extension - Re-route 11kV Double circuit conductors on new poles. Remove Temp Links on pole 21600. Remove Temp SW '347'
|  | O-15742-A | Kaiatea |  | Ngunguru CB1072 | 2024-10-17 09:08 | 45582.3806 | 2024-10-17 15:09 | 45582.6312 | 0.16826 | 0.00046609 | 30 | 10830 | Planned | Planned Interruption | Network Extension re-locate poles and install new 30kVA tx NP308
|  | O-15355-A | Jordan Valley |  | Hikurangi CB1102 | 2024-10-17 11:04 | 45582.4611 | 2024-10-17 13:25 | 45582.559 | 0.10953 | 0.00077681 | 50 | 7050 | Planned | Planned Interruption | Replace Pole #35782 with B11
|  | O-15922-A | Hakaru |  | Kaiwaka CB1032 | 2024-10-17 11:31 | 45582.4799 | 2024-10-17 12:22 | 45582.5153 | 0.33041 | 0.0064786 | 417 | 21267 | Planned | Planned Interruption | Improvements in Supply Quality. Installing New switch 10174 on pole 411926.
|  | F-7813-A | Fert. Works |  | Kioreroa CB6 | 2024-10-18 09:07 | 45583.3799 | 2024-10-18 09:54 | 45583.4125 | 0.007302 | 0.00015536 | 10 | 470 | Unplanned | Defective Equipment | FP387385 Broken HV binder @ pole 62490
|  | F-7816-A | Whakapara |  | Hikurangi CB1112 | 2024-10-20 06:15 | 45585.2601 | 2024-10-20 10:49 | 45585.4507 | 0.57169 | 0.0067272 | 433 | 36797 | Unplanned | Defective Equipment | FP 387427 - 11kV jumper KB511 fault
|  | O-15970-A | Maunu Road |  | Whangarei South CB1102 | 2024-10-20 09:05 | 45585.3785 | 2024-10-20 15:45 | 45585.6562 | 0.37909 | 0.00094771 | 61 | 24400 | Planned | Planned Interruption | OHUG Tx CONVERSION. INSTALL NEW GM Tx's WC469, WC470 & REMOVE EXISTING OH Tx WC322. 61 ICPs to be added to Trouble Order
|  | F-7819-A | Kaka St |  | Whangarei South CB1032 | 2024-10-20 13:32 | 45585.5639 | 2024-10-20 14:08 | 45585.5889 | 0.19745 | 0.0057795 | 372 | 12709 | Unplanned | Vegetation | FP 387431 - Patrolled - Palm branch removed from 11kV - repeat offender. Follow up required to remove palm tree pls.
|  | O-16090-A | Brynderwyn |  | Maungaturoto CB1 | 2024-10-22 09:02 | 45587.3764 | 2024-10-22 15:26 | 45587.6431 | 0.041762 | 0.00010875 | 7 | 2688 | Planned | Planned Interruption | Network Maintenance - relocate TX out of drain area
|  | O-16009-A | Taipuha |  | Mareretu CB1 | 2024-10-22 09:10 | 45587.3819 | 2024-10-22 12:48 | 45587.5333 | 0.0033869 | 1.5536e-05 | 1 | 218 | Planned | Planned Interruption | Replace poles 34238 and 34239.
|  | O-15784-A | Onoke |  | Kamo CB8 | 2024-10-22 09:16 | 45587.3861 | 2024-10-22 12:53 | 45587.5368 | 0.067427 | 0.00031073 | 20 | 4340 | Planned | Planned Interruption | Upgrade pole mount Tx KV122 from a 50kva to a 75kva. Upgrade HT jumpers to 35mm copper.
|  | O-15334-A | Ruawai Town |  | Ruawai CB1072 | 2024-10-22 09:17 | 45587.3868 | 2024-10-22 15:06 | 45587.6292 | 0.32533 | 0.00093218 | 60 | 20940 | Planned | Planned Interruption | Replace pole, replace crossarms, straighten poles and upgrade F201 to 50KVA
|  | O-15748-A | Taipuha |  | Mareretu CB1 | 2024-10-23 09:01 | 45588.3757 | 2024-10-23 12:55 | 45588.5382 | 0.14906 | 0.00063699 | 41 | 9594 | Planned | Planned Interruption | Replace HV cross arms and pole 33695
|  | O-15712-A | Paranui |  | Tikipunga CB6 | 2024-10-23 09:03 | 45588.3772 | 2024-10-23 12:12 | 45588.5086 | 0.38213 | 0.0020197 | 130 | 24596 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #51360 to the end of line
|  | O-15349-A | Te Kopuru |  | Dargaville CB2 | 2024-10-23 09:04 | 45588.3778 | 2024-10-23 16:58 | 45588.7069 | 0.42712 | 0.0009011 | 58 | 27492 | Planned | Planned Interruption | Network Maintenance - pole replacement & replacing LV conductor under 11kV lines
|  | O-16099-A | Thelma Road |  | Mangawhai North CB4 | 2024-10-23 09:09 | 45588.3812 | 2024-10-23 13:15 | 45588.5521 | 0.068795 | 0.00027965 | 18 | 4428 | Planned | Planned Interruption | Level transformer
|  | F-7831-A | Ararua |  | Mareretu CB2 | 2024-10-23 14:56 | 45588.6222 | 2024-10-23 16:52 | 45588.7028 | 0.018022 | 0.00015536 | 10 | 1160 | Unplanned | Defective Equipment | 387498 / Carry out repairs to broken 11kV binder and spragged LV below.
|  | O-16174-A | Fert. Works |  | Kioreroa CB6 | 2024-10-23 15:55 | 45588.6632 | 2024-10-23 17:01 | 45588.709 | 0.0020508 | 3.1073e-05 | 2 | 132 | Planned | Planned Interruption | Network Maintenance Cleaning Tx room & install fire detector
|  | F-7834-A | Paparoa |  | Mareretu CB6 | 2024-10-23 20:07 | 45588.8382 | 2024-10-23 21:31 | 45588.8966 | 0.31484 | 0.0091819 | 591 | 20265 | Unplanned | Unknown | 387505 Report of loud bang near Y184 - nothing found. suspect a bird strike near
|  | O-15871-A | Titoki |  | Poroti CB1032 | 2024-10-24 09:02 | 45589.3764 | 2024-10-24 13:37 | 45589.5674 | 0.1709 | 0.00062145 | 40 | 11000 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #50468 to pole #334448
|  | O-16051-A | King Road |  | Mangawhai North CB2 | 2024-10-24 21:32 | 45589.8975 | 2024-10-25 03:08 | 45590.1303 | 4.2389 | 0.012647 | 814 | 272839 | Planned | Planned Interruption | Replace Transformer MC287 like for like. Replace HV and LV hardware & straighten poles
|  | O-15874-A | Tangowahine |  | Dargaville CB8 | 2024-10-25 09:35 | 45590.3993 | 2024-10-25 15:20 | 45590.6389 | 0.19296 | 0.00055931 | 36 | 12420 | Planned | Planned Interruption | POLE & HARDWARE REPLACEMENTS
|  | F-7843-A | Dunns Rd |  | Ruawai CB1082 | 2024-10-26 05:02 | 45591.2095 | 2024-10-26 09:42 | 45591.4042 | 0.31517 | 0.0056397 | 363 | 20286 | Unplanned | Third Party Interference | 387585/ Car v Pole Event No. 4075094
|  | O-16258-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2024-10-29 09:33 | 45594.3979 | 2024-10-29 12:01 | 45594.5007 | 0.089675 | 0.00060591 | 39 | 5772 | Planned | Planned Interruption | Clear trees around lines from pole #49334 to the end of line
|  | O-16168-A | Wairere |  | Mareretu CB5 | 2024-10-29 09:41 | 45594.4035 | 2024-10-29 13:25 | 45594.559 | 0.017401 | 7.7681e-05 | 5 | 1120 | Planned | Planned Interruption | Transformer Upgrade (15 to 50kVA for existing pump as it has been changed from submain to normal connection with ICP
|  | O-15907-A | Hakaru |  | Kaiwaka CB1032 | 2024-10-30 09:03 | 45595.3771 | 2024-10-30 12:09 | 45595.5062 | 0.4439 | 0.0025324 | 163 | 28572 | Planned | Planned Interruption | Installing New Switch 10184 on Pole 47137. Removing Fuses 422 on Pole 334460. Replace tx MC218
|  | O-16012-A | Tangowahine |  | Dargaville CB8 | 2024-10-30 09:12 | 45595.3833 | 2024-10-30 15:06 | 45595.6292 | 0.20349 | 0.00057484 | 37 | 13098 | Planned | Planned Interruption | Network Maintenance - HV ARM REPLACEMENTS FROM POLES 37867 & 37863 TO EOL
|  | F-7867-A | Ararua |  | Mareretu CB2 | 2024-10-30 10:23 | 45595.4326 | 2024-10-30 11:44 | 45595.4889 | 0.0088091 | 0.00010875 | 7 | 567 | Unplanned | Other Cause | 387528 Low lines - mid span pole to be installed
|  | O-15859-A | Waipu |  | Ruakaka CB2 | 2024-10-30 10:33 | 45595.4398 | 2024-10-30 14:02 | 45595.585 | 0.55205 | 0.0026412 | 170 | 35533 | Planned | Planned Interruption | Replacing 11kv pole 10509 & Fuses 546 with new switch 10182.
|  | O-15910-A | Hakaru |  | Kaiwaka CB1032 | 2024-10-31 09:02 | 45596.3764 | 2024-10-31 12:22 | 45596.5153 | 0.39259 | 0.0022062 | 142 | 25269 | Planned | Planned Interruption | Removing Fuses 367 (pole 47073) Installing New Switch 10185 (pole 47073) in the open position
|  | O-16015-A | North Dargaville |  | Dargaville CB1 | 2024-10-31 09:04 | 45596.3778 | 2024-10-31 13:14 | 45596.5514 | 0.042725 | 0.0001709 | 11 | 2750 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #27079 to pole #27081
|  | O-16246-A | Mains Ave |  | Tikipunga CB2 | 2024-10-31 09:06 | 45596.3792 | 2024-10-31 12:03 | 45596.5021 | 0.73973 | 0.0041793 | 269 | 47613 | Planned | Planned Interruption | Network Extension install new 11kV cable and transformer WC474
|  | O-15976-A | Marsden Pt |  | Ruakaka CB1 | 2024-10-31 09:18 | 45596.3875 | 2024-10-31 12:49 | 45596.534 | 0.44911 | 0.0021285 | 137 | 28907 | Planned | Planned Interruption | Repair Leaking bushing tx RP377
|  | O-16156-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2024-10-31 09:32 | 45596.3972 | 2024-10-31 11:30 | 45596.4792 | 0.011 | 9.3218e-05 | 6 | 708 | Planned | Planned Interruption | Replace like for like 30kVA TX - C351
|  | F-7870-A | Tangaihi |  | Ruawai CB1032 | 2024-10-31 19:16 | 45596.8028 | 2024-10-31 19:34 | 45596.8153 | 0.0022372 | 0.00012429 | 8 | 144 | Unplanned | Vegetation | FP 387739 - Branch in line near pole 28473
|  | F-7873-A | Turiwiri |  | Dargaville CB9 | 2024-10-31 19:21 | 45596.806 | 2024-10-31 19:36 | 45596.8163 | 0.038577 | 0.0077681 | 500 | 2483 | Unplanned | Unknown | FPIs on Sw 2152 ABC phase.
|  | F-7876-A | Marsden Bay |  | Bream Bay CB1107 | 2024-11-01 01:04 | 45597.0444 | 2024-11-01 02:47 | 45597.116 | 0.039989 | 0.00038824 | 25 | 2575 | Unplanned | Wildlife | F 4078452 / FP 387741 - FENZ call for pole on fire. Found possum on crucifix, 2 blown HV fuses RO394
|  | O-16348-A | Paranui |  | Tikipunga CB6 | 2024-11-01 09:10 | 45597.3819 | 2024-11-01 11:35 | 45597.4826 | 0.0022518 | 1.553e-05 | 1 | 145 | Planned | Planned Interruption | 15kVA to 50kVA upgrade
|  | F-7885-A | Paranui |  | Tikipunga CB6 | 2024-11-01 19:47 | 45597.8243 | 2024-11-02 01:55 | 45598.0799 | 0.01143 | 3.1059e-05 | 2 | 736 | Unplanned | Defective Equipment | Replace faulty tx
|  | F-7888-A | Jordan Valley |  | Hikurangi CB1102 | 2024-11-02 08:54 | 45598.3708 | 2024-11-02 12:29 | 45598.5204 | 0.42489 | 0.014784 | 952 | 27360 | Unplanned | Defective Equipment | FP387773 Line down @ pole 35013 towards pole 324337, Also replaced blown lightning arrester @ Tx KS142
|  | O-16135-A | 2nd Ave |  | Alexander St CB3 | 2024-11-03 08:34 | 45599.3569 | 2024-11-03 21:29 | 45599.8951 | 1.0618 | 0.0020499 | 132 | 68371 | Planned | Planned Interruption | Replace RMU with safelink. Outage on HV ended at 2129pm but customers were generated from 1710 as shutdown went well overtime.
|  | F-7891-A | Tangaihi |  | Ruawai CB1032 | 2024-11-03 22:15 | 45599.9268 | 2024-11-03 23:41 | 45599.9871 | 0.17662 | 0.0020344 | 131 | 11373 | Unplanned | Defective Equipment | 387781 / Isolate to repair HV binder on pole 28765.
|  | O-15400-A | Tangowahine |  | Dargaville CB8 | 2024-11-04 09:13 | 45600.384 | 2024-11-04 15:32 | 45600.6472 | 0.064743 | 0.00017083 | 11 | 4169 | Planned | Planned Interruption | Install links 10200, Pole changes & associated works
|  | O-16189-A | Langs Beach |  | Mangawhai North CB3 | 2024-11-04 09:19 | 45600.3882 | 2024-11-04 13:18 | 45600.5542 | 0.18187 | 0.00076095 | 49 | 11711 | Planned | Planned Interruption | Network Maintenance - level transformers MC499 and MC500
|  | O-16018-A | Tangaihi |  | Ruawai CB1032 | 2024-11-04 09:32 | 45600.3974 | 2024-11-04 14:28 | 45600.6027 | 0.28012 | 0.00094731 | 61 | 18038 | Planned | Planned Interruption | Clear trees around 11kv line from pole #19189 to pole #331282
|  | F-7897-A | Waipu |  | Ruakaka CB2 | 2024-11-04 20:27 | 45600.8521 | 2024-11-04 23:05 | 45600.9618 | 0.29444 | 0.0018636 | 120 | 18960 | Unplanned | Defective Equipment | FP 387820 HV line down at pole 10525 (pole 10526 side)
|  | O-16363-A | Swamp North |  | Hikurangi CB1042 | 2024-11-05 09:02 | 45601.3767 | 2024-11-05 11:12 | 45601.4666 | 0.30155 | 0.0023294 | 150 | 19418 | Planned | Planned Interruption | Upgrade tx from 30kVA to 50kVA & Replace LAs
|  | O-16192-A | Langs Beach |  | Mangawhai North CB3 | 2024-11-05 09:25 | 45601.3924 | 2024-11-05 11:14 | 45601.4681 | 0.098178 | 0.00090072 | 58 | 6322 | Planned | Planned Interruption | Network Maintenance - Level Transformer
|  | O-15937-A | Hokianga Rd |  | Dargaville CB7 | 2024-11-05 09:26 | 45601.3931 | 2024-11-05 15:23 | 45601.641 | 0.2772 | 0.00077648 | 50 | 17850 | Planned | Planned Interruption | Dismantle pothead and x-arm at pole 54006. Replace 11kV riser from base of pole
|  | O-15790-A | Tangowahine |  | Dargaville CB8 | 2024-11-06 09:09 | 45602.3812 | 2024-11-06 13:36 | 45602.5667 | 0.029025 | 0.00010871 | 7 | 1869 | Planned | Planned Interruption | Network Maintenance - Pole & x-arm changes
|  | O-15403-A | Hokianga Rd |  | Dargaville CB7 | 2024-11-06 09:15 | 45602.3854 | 2024-11-06 14:25 | 45602.6007 | 0.024071 | 7.7648e-05 | 5 | 1550 | Planned | Planned Interruption | Removed DA70, Install DA140. Incorrect customers logged, due to Tx replacement-Patch process issue.
|  | O-16138-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-11-07 09:03 | 45603.3771 | 2024-11-07 14:34 | 45603.6069 | 0.41122 | 0.0012424 | 80 | 26480 | Planned | Planned Interruption | Re-route HV line, connect & liven 2x new 50kVA Tx C546 & C547
|  | O-16276-A | Kiripaka Rd |  | Tikipunga CB8 | 2024-11-07 09:05 | 45603.3785 | 2024-11-07 14:21 | 45603.5979 | 0.063796 | 0.00020189 | 13 | 4108 | Planned | Planned Interruption | Replacing Poles & Conductor from poles 40319-40320 & 40323.
|  | F-7945-A | Maungakaramea |  | Maungatapere CB3 | 2024-11-07 14:05 | 45603.5868 | 2024-11-07 14:57 | 45603.6229 | 0.014536 | 0.00027953 | 18 | 936 | Unplanned | Defective Equipment | 387949 Jumper off insulator at pole 21823
|  | O-16261-A | Matapouri |  | Ngunguru CB1032 | 2024-11-08 09:04 | 45604.3778 | 2024-11-08 11:17 | 45604.4701 | 0.014458 | 0.00010871 | 7 | 931 | Planned | Planned Interruption | Level D-sub NT118
|  | O-16285-A | Springs Flat |  | Kamo CB1 | 2024-11-08 09:05 | 45604.3785 | 2024-11-08 15:29 | 45604.6451 | 0.059634 | 0.0001553 | 10 | 3840 | Planned | Planned Interruption | -Replacing 11kv Poles, terminating NEW UG cable & VLF testing -Installing New Automated Switch 10165 at pole 40326
|  | F-7951-A | Whakapara |  | Hikurangi CB1112 | 2024-11-08 13:58 | 45604.5819 | 2024-11-08 14:36 | 45604.6083 | 0.034817 | 0.00091625 | 59 | 2242 | Unplanned | Defective Equipment | 387967 - Spragged lines
|  | O-16288-A | Springs Flat |  | Kamo CB1 | 2024-11-10 09:02 | 45606.3764 | 2024-11-10 13:39 | 45606.5687 | 0.35805 | 0.0013666 | 88 | 23056 | Planned | Planned Interruption | Connecting 11kV cable at pole 40326 & pole 40323, Installing 11kv Breaks at pole 20372 & pole 17566 & liven new config
|  | O-15787-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-11-10 09:04 | 45606.3778 | 2024-11-10 12:16 | 45606.5111 | 0.22363 | 0.0011647 | 75 | 14400 | Planned | Planned Interruption | Crucifix and DOFs installed at pole 304807 and labelled 10191. 3 phase 50kva ground mount TX C545
|  | F-7963-A | Jordan Valley |  | Hikurangi CB1102 | 2024-11-11 09:40 | 45607.4028 | 2024-11-11 12:59 | 45607.5408 | 0.24138 | 0.0073921 | 476 | 15543 | Unplanned | Defective Equipment | FP388016 EF - HV jumper touching polly at pole 35013
|  | F-7966-A | Treatment |  | Kioreroa CB2 | 2024-11-11 10:43 | 45607.4465 | 2024-11-11 11:08 | 45607.4638 | 0.086888 | 0.0034942 | 225 | 5595 | Unplanned | Third Party Interference | FP388023 Truck contacted HV lines between pole 304036 & 65238 - Faultman checked network and advised safe to liven
|  | O-16216-A | Springs Flat |  | Kamo CB1 | 2024-11-12 09:01 | 45608.3756 | 2024-11-12 13:31 | 45608.563 | 0.40237 | 0.0014908 | 96 | 25910 | Planned | Planned Interruption | Network Maintenance - HV/LV ARM & HARDWARE REPLACEMENTS
|  | O-4738-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2024-11-12 09:24 | 45608.3917 | 2024-11-12 13:35 | 45608.566 | 1.6292 | 0.0064914 | 418 | 104911 | Planned | Planned Interruption | Network Extension - Install new pole and 50kva 3 phase TX labelled C548 between poles 49080 and 49081 Upgrade LV overhead lines
|  | F-7972-A | Bickerstaff |  | Maungaturoto CB2 | 2024-11-12 17:51 | 45608.7435 | 2024-11-12 22:15 | 45608.9271 | 0.31452 | 0.012051 | 776 | 20253 | Unplanned | Defective Equipment | FP388076 Feeder tripped E/F - Customer reported blown @ Tx D180
|  | O-16675-A | Okara Drive |  | Whangarei South CB1092 | 2024-11-13 00:17 | 45609.0118 | 2024-11-13 03:23 | 45609.141 | 0.76527 | 0.0042396 | 273 | 49278 | Unplanned | Defective Equipment | FP388077 Sw 253 oil leak - low oil - oil top up & repair works
|  | O-15058-A | Access Rd |  | Ruawai CB1022 | 2024-11-13 09:01 | 45609.3759 | 2024-11-13 14:08 | 45609.5889 | 0.56206 | 0.0018325 | 118 | 36193 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-4840-B | Marsden South |  | Bream Bay CB1111 | 2024-11-13 12:25 | 45609.5174 | 2024-11-13 16:10 | 45609.6736 | 0.0034942 | 1.553e-05 | 1 | 225 | Planned | Planned Interruption | Network Maintenance Leaking bushing & insulation work
|  | O-16390-A | Swamp North |  | Hikurangi CB1042 | 2024-11-14 09:06 | 45610.3792 | 2024-11-14 14:50 | 45610.6181 | 0.28314 | 0.00082307 | 53 | 18232 | Planned | Planned Interruption | Network Maintenance - HV HARDWARE AND WIRE REPLACEMENT
|  | O-16480-A | Ararua |  | Mareretu CB2 | 2024-11-14 09:08 | 45610.3806 | 2024-11-14 15:48 | 45610.6583 | 1.2734 | 0.0031836 | 205 | 82000 | Planned | Planned Interruption | Replace Poles 48964, 48027, 48028 Ran 40min over due to work taking longer than anticipated
|  | O-16417-A | ToeToe Rd |  | Kioreroa CB7 | 2024-11-15 09:02 | 45611.3764 | 2024-11-15 13:32 | 45611.5639 | 0.15933 | 0.00059013 | 38 | 10260 | Planned | Planned Interruption | Network Extension - install new pole and HV links, ready for further works.
|  | O-16273-A | Tangowahine |  | Dargaville CB8 | 2024-11-15 09:32 | 45611.3969 | 2024-11-15 11:32 | 45611.4806 | 0.069309 | 0.0005746 | 37 | 4463 | Planned | Planned Interruption | Replace guy wire pole beneath 11kv line from Pole #37324 to Pole #36856
|  | F-8023-A | Puwera |  | Maungatapere CB7 | 2024-11-17 08:02 | 45613.3347 | 2024-11-17 11:09 | 45613.4646 | 0.051652 | 0.00059013 | 38 | 3326 | Unplanned | Defective Equipment | 388165 / Broken DDO at Tx X348 requiring replacement. All 3 replaced.
|  | F-8029-A | Maungakaramea |  | Maungatapere CB3 | 2024-11-17 12:32 | 45613.5222 | 2024-11-17 17:14 | 45613.7181 | 0.34644 | 0.0020654 | 133 | 22308 | Unplanned | Vegetation | Fault Trip B & C Phase. Found tree on lines at pole 53736 causing damage to two conductors. Repaired & BTN
|  | F-8347-A | Paranui |  | Tikipunga CB6 | 2024-11-18 07:52 | 45614.3278 | 2024-12-28 15:09 | 45654.6312 | 0.92967 | 0.011321 | 1454 | 60468 | Unplanned | Defective Equipment | 389137/ Broken Xarm
|  | F-8044-A | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2024-11-19 09:18 | 45615.3873 | 2024-11-19 09:34 | 45615.3985 | 0.072322 | 0.0045812 | 295 | 4657 | Unplanned | Unknown | Tripped O/C A&B phase - Unknown cause
|  | F-8053-A | Titoki |  | Poroti CB1032 | 2024-11-19 14:57 | 45615.6232 | 2024-11-19 15:01 | 45615.6256 | 0.01348 | 0.0040222 | 259 | 868 | Unplanned | Third Party Interference | FP388232 Foil balloon caught in overhead lines mid-span
|  | F-8056-A | Pataua |  | Parua Bay CB1 | 2024-11-20 03:12 | 45616.1333 | 2024-11-20 03:29 | 45616.1449 | 0.18056 | 0.014738 | 949 | 11627 | Unplanned | Unknown | Trip Overcurrent A & B. Closed in BTN
|  | O-4720-B | Springs Flat |  | Kamo CB1 | 2024-11-20 09:07 | 45616.3797 | 2024-11-20 14:27 | 45616.6019 | 0.97894 | 0.0030593 | 197 | 63037 | Planned | Planned Interruption | Network Maintenance REPLACE HV POLES, ARMS & HARDWARE. UPGRADE OH LV.
|  | O-4789-B | Ararua |  | Mareretu CB2 | 2024-11-20 09:55 | 45616.4132 | 2024-11-20 16:17 | 45616.6785 | 0.56686 | 0.0015685 | 101 | 36502 | Planned | Planned Interruption | Network Maintenance - Replace poles, crossarms & structures at various locations
|  | F-8059-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2024-11-20 11:50 | 45616.4928 | 2024-11-20 12:16 | 45616.511 | 0.16954 | 0.0064914 | 418 | 10917 | Unplanned | Unknown | F-8059-A. Int fault. FPIs indicating betwn Sw 332 & 333 - relocated. RCB returned (Trees) B4 relivening. MP to download 1508
|  | O-4780-B | Hakaru |  | Kaiwaka CB1032 | 2024-11-21 09:04 | 45617.3778 | 2024-11-21 12:10 | 45617.5069 | 0.0086655 | 4.6589e-05 | 3 | 558 | Planned | Planned Interruption | Network Maintenance - replace pole 11985
|  | O-15178-A | Turiwiri |  | Dargaville CB9 | 2024-11-21 09:27 | 45617.3937 | 2024-11-21 14:42 | 45617.6122 | 0.2541 | 0.00080754 | 52 | 16362 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-4717-B | ToeToe Rd |  | Kioreroa CB7 | 2024-11-22 09:04 | 45618.3778 | 2024-11-22 14:08 | 45618.5889 | 0.056652 | 0.00018636 | 12 | 3648 | Planned | Planned Interruption | Connect new 11kV cable up new pole and onto HV links 10217 - O209 isolated for access through LV
|  | O-4735-B | Puwera |  | Maungatapere CB7 | 2024-11-22 09:04 | 45618.3778 | 2024-11-22 14:27 | 45618.6021 | 0.75432 | 0.002345 | 151 | 48573 | Planned | Planned Interruption | Maungatapere CB7 : 92 MAUNGAKARAMEA RD : Network Maintenance
|  | O-4834-B | North River |  | Ruakaka CB7 | 2024-11-22 09:07 | 45618.3799 | 2024-11-22 14:59 | 45618.6243 | 0.15853 | 0.00045036 | 29 | 10208 | Planned | Planned Interruption | Network Maintenance - replace TX RB144 like for like and replace pole hardware
|  | F-8098-A | Bickerstaff |  | Maungaturoto CB2 | 2024-11-22 13:51 | 45618.5771 | 2024-11-22 15:46 | 45618.6569 | 0.035718 | 0.00031059 | 20 | 2300 | Unplanned | Defective Equipment | 388335 - broken binder pole 333289
|  | O-16207-A | Kaka St |  | Whangarei South CB1032 | 2024-11-24 08:31 | 45620.3549 | 2024-11-24 18:27 | 45620.7688 | 0.12958 | 0.00021741 | 14 | 8344 | Planned | Planned Interruption | Replace Total Sub WC219 (RMU & Tx Unit)
|  | O-4768-B | Brynderwyn |  | Maungaturoto CB1 | 2024-11-24 09:01 | 45620.3757 | 2024-11-24 11:46 | 45620.4903 | 0.10762 | 0.00065224 | 42 | 6930 | Planned | Planned Interruption | Network Maintenance - REPLACE CONDUCTOR BETWEEN POLES 909852 TO POLE 909701
|  | F-8104-A | Titoki |  | Poroti CB1032 | 2024-11-24 12:36 | 45620.5251 | 2024-11-24 14:02 | 45620.5847 | 0.0026711 | 3.1059e-05 | 2 | 172 | Unplanned | Wildlife | 388363 / 3 x HV fuses blown due to possum. BTN
|  | O-4750-B | Marsden Bay |  | Bream Bay CB1107 | 2024-11-25 09:42 | 45621.4042 | 2024-11-25 13:55 | 45621.5799 | 0.015716 | 6.2119e-05 | 4 | 1012 | Planned | Planned Interruption | Tx STRUCTURE REFURBISHMENT, REPLANT OFF FACE POLE
|  | F-8110-A | Thelma Road |  | Mangawhai North CB4 | 2024-11-25 10:14 | 45621.4267 | 2024-11-25 11:50 | 45621.4931 | 0.50168 | 0.016927 | 1090 | 32305 | Unplanned | Third Party Interference | 338379 - cable struck by fencing worker
|  | O-4816-B | Onoke |  | Kamo CB8 | 2024-11-26 09:04 | 45622.3778 | 2024-11-26 14:22 | 45622.5986 | 0.019754 | 6.2119e-05 | 4 | 1272 | Planned | Planned Interruption | Vegetation clearing 11kv lines from Issuer earths at pole #52755 to the end of line
|  | O-15760-A | Taipuha |  | Mareretu CB1 | 2024-11-26 09:05 | 45622.3785 | 2024-11-26 09:29 | 45622.3951 | 0.021617 | 0.00090072 | 58 | 1392 | Planned | Planned Interruption | Replace HV & LV cross arms. Remove redundant LV circuit. *Job abandoned soon after starting due to no Generation at school*
|  | O-4831-B | Dunns Rd |  | Ruawai CB1082 | 2024-11-26 09:08 | 45622.3806 | 2024-11-26 12:21 | 45622.5146 | 0.1109 | 0.0005746 | 37 | 7141 | Planned | Planned Interruption | Network Maintenance - Install dampers and rebind HV
|  | O-15850-A | Titoki |  | Poroti CB1032 | 2024-11-27 09:02 | 45623.3764 | 2024-11-27 12:39 | 45623.5271 | 0.02022 | 9.3178e-05 | 6 | 1302 | Planned | Planned Interruption | Replace poles, establish new Tx's P503 on pole 50446 & Disestablish T P190 from pole 50447.
|  | O-4792-B | Ararua |  | Mareretu CB2 | 2024-11-27 09:04 | 45623.3778 | 2024-11-27 12:45 | 45623.5312 | 0.34664 | 0.0015685 | 101 | 22321 | Planned | Planned Interruption | Network Renewal - Reconductor 11kV lines from H Structure Pole 48027 - 48028 to EOL
|  | F-8116-A | Wairere |  | Mareretu CB5 | 2024-11-28 06:37 | 45624.2757 | 2024-11-28 13:31 | 45624.5632 | 0.72758 | 0.0070505 | 454 | 46851 | Unplanned | Defective Equipment | FP388484 - Unable to bfd Sw381 remotely (Sw 6202 still manual). Sectionalised and patrolled. 2nd man from WHG. HV jumper on xarm
|  | O-16438-A | Maungakaramea |  | Maungatapere CB3 | 2024-11-28 09:08 | 45624.3806 | 2024-11-28 13:30 | 45624.5625 | 0.10436 | 0.00060566 | 39 | 6720 | Planned | Planned Interruption | Replace sw 872 with sw 10172 on adjacent switch
|  | O-16141-A | Brynderwyn |  | Maungaturoto CB1 | 2024-11-28 09:18 | 45624.3875 | 2024-11-28 14:06 | 45624.5875 | 0.27282 | 0.00094731 | 61 | 17568 | Planned | Planned Interruption | replace cross arms, ampacts, upgrade D320
|  | O-4771-B | Hakaru |  | Kaiwaka CB1032 | 2024-11-29 09:04 | 45625.3778 | 2024-11-29 14:25 | 45625.6007 | 0.2343 | 0.00072989 | 47 | 15087 | Planned | Planned Interruption | Kaiwaka CB1032 : Shut 1 - Brown Road Hakaru : Network Maintenance
|  | O-4960-B | Mains Ave |  | Tikipunga CB2 | 2024-11-29 09:09 | 45625.3812 | 2024-11-29 15:14 | 45625.6347 | 0.37978 | 0.0010405 | 67 | 24455 | Planned | Planned Interruption | Connect new TX WC474
|  | O-4828-B | Mata |  | Ruakaka CB3 | 2024-11-29 09:12 | 45625.3833 | 2024-11-29 15:11 | 45625.6326 | 0.16725 | 0.00046589 | 30 | 10770 | Planned | Planned Interruption | Cut vegetation 11kv lines from pole #60890 to the end of line
|  | O-4873-B | Rewa Rewa Rd |  | Whangarei South CB1082 | 2024-11-29 12:30 | 45625.5208 | 2024-11-29 12:43 | 45625.5299 | 0.010094 | 0.00077648 | 50 | 650 | Planned | Planned Interruption | Change tap on TX WO226
|  | F-8128-A | Kokopu |  | Poroti CB1022 | 2024-11-30 16:07 | 45626.6715 | 2024-11-30 21:37 | 45626.9007 | 0.62827 | 0.0063361 | 408 | 40456 | Unplanned | Defective Equipment | FP388536 - broken HV jumper on crossarm damaged equipment
|  | O-4774-B | Puwera |  | Maungatapere CB7 | 2024-12-02 09:06 | 45628.3792 | 2024-12-02 14:17 | 45628.5951 | 0.68073 | 0.0021888 | 141 | 43851 | Planned | Planned Interruption | POLE, CONDUCTOR & HARDWARE REPLACEMENTS
|  | O-4879-B | Maungakaramea |  | Maungatapere CB3 | 2024-12-02 09:10 | 45628.3819 | 2024-12-02 13:49 | 45628.5757 | 0.017324 | 6.2094e-05 | 4 | 1116 | Planned | Planned Interruption | Tree clearing work
|  | O-4714-B | One Tree Point |  | Ruakaka CB6 | 2024-12-02 09:56 | 45628.4139 | 2024-12-02 14:22 | 45628.5986 | 0.0082586 | 3.1047e-05 | 2 | 532 | Planned | Planned Interruption | Upgrade ground mount D-sub Ro416 from 200kva to 500kva
|  | O-16096-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2024-12-02 10:05 | 45628.4198 | 2024-12-02 14:47 | 45628.6156 | 0.57347 | 0.0020336 | 131 | 36942 | Planned | Planned Interruption | -Replace crossarms 23177 and install permanant break -Installing access rd RMU
|  | F-8140-A | ToeToe Rd |  | Kioreroa CB7 | 2024-12-02 10:48 | 45628.45 | 2024-12-02 11:03 | 45628.4607 | 0.10913 | 0.009516 | 613 | 7030 | Unplanned | Unknown | Nil / Overcurrent B Phase. 15 Min Closed & BTN
|  | F-8143-A | One Tree Point |  | Ruakaka CB6 | 2024-12-02 15:28 | 45628.6444 | 2024-12-02 15:34 | 45628.6486 | 0.00018628 | 3.1047e-05 | 2 | 12 | Unplanned | Human Error | Re Isolate to Upgrade fusing that was missed during installation on O-4714-B
|  | O-15472-A | Titoki |  | Poroti CB1032 | 2024-12-03 09:03 | 45629.3771 | 2024-12-03 14:01 | 45629.584 | 0.064765 | 0.00021733 | 14 | 4172 | Planned | Planned Interruption | Replace HV arms and Refurbish Dsub TW128
|  | O-15445-A | Turiwiri |  | Dargaville CB9 | 2024-12-03 09:05 | 45629.3785 | 2024-12-03 14:05 | 45629.5868 | 0.18628 | 0.00062094 | 40 | 12000 | Planned | Planned Interruption | Replace HV & LV cross arms
|  | O-15427-A | Titoki |  | Poroti CB1032 | 2024-12-03 09:07 | 45629.3799 | 2024-12-03 11:34 | 45629.4819 | 0.057049 | 0.00038809 | 25 | 3675 | Planned | Planned Interruption | Replace HV pole 18190 and HV arms on various poles.
|  | O-4795-B | Puwera |  | Maungatapere CB7 | 2024-12-04 09:03 | 45630.3771 | 2024-12-04 12:58 | 45630.5403 | 0.51437 | 0.0021888 | 141 | 33135 | Planned | Planned Interruption | Network Maintenance - POLE, CONDUCTOR & HARDWARE REPLACEMENTS
|  | O-15550-A | Ararua |  | Mareretu CB2 | 2024-12-04 09:05 | 45630.3785 | 2024-12-04 13:15 | 45630.5521 | 0.0077618 | 3.1047e-05 | 2 | 500 | Planned | Planned Interruption | Refurbish Dsubs A152 and A153 Network Maintenance
|  | O-4723-B | Charles St |  | Kamo CB2 | 2024-12-04 09:05 | 45630.3785 | 2024-12-04 15:37 | 45630.6507 | 0.46856 | 0.0011953 | 77 | 30184 | Planned | Planned Interruption | Replace Oil Switch 7974-7345-7348-7346.
|  | F-8149-A | Marsden South |  | Bream Bay CB1111 | 2024-12-04 16:50 | 45630.7016 | 2024-12-04 19:40 | 45630.8194 | 0.002639 | 1.5524e-05 | 1 | 170 | Unplanned | Unknown | 388645 / Isolate to replace blown Fuse on Sw 5287. No Cause Found.
|  | O-15094-A | Turiwiri |  | Dargaville CB9 | 2024-12-05 09:01 | 45631.3757 | 2024-12-05 14:20 | 45631.5971 | 0.46024 | 0.0014437 | 93 | 29648 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-4798-B | Whatatiri |  | Maungatapere CB8 | 2024-12-05 09:03 | 45631.3771 | 2024-12-05 10:07 | 45631.4215 | 0.094384 | 0.0014747 | 95 | 6080 | Planned | Planned Interruption | Clear trees around 11kv lines from pole #60268 to pole #60345
|  | O-4855-B | Marsden Pt |  | Ruakaka CB1 | 2024-12-05 09:09 | 45631.3812 | 2024-12-05 11:26 | 45631.4764 | 0.11059 | 0.00080723 | 52 | 7124 | Planned | Planned Interruption | Voltage indicator replacement
|  | F-8152-A | Cartwright Rd |  | Onerahi CB6 | 2024-12-05 22:08 | 45631.9222 | 2024-12-05 23:30 | 45631.9792 | 0.74339 | 0.0090658 | 584 | 47888 | Unplanned | Defective Equipment | FP 388664 Repair HV jumper @ Sw 9431 & Clear Vegetation from 11kV
|  | O-4786-B | Hakaru |  | Kaiwaka CB1032 | 2024-12-06 09:01 | 45632.3754 | 2024-12-06 12:59 | 45632.5413 | 0.014825 | 6.2094e-05 | 4 | 955 | Planned | Planned Interruption | Network Maintenance - replace poles and crossarms between poles 45962 and 327439
|  | O-4882-B | Ararua |  | Mareretu CB2 | 2024-12-06 09:10 | 45632.3819 | 2024-12-06 14:36 | 45632.6083 | 0.060728 | 0.00018628 | 12 | 3912 | Planned | Planned Interruption | Upgrade TX Y100 and Y168
|  | O-4852-B |  |  |  | 2024-12-06 10:01 | 45632.4173 | 2024-12-06 11:49 | 45632.4927 | 0.22247 | 0.0020491 | 132 | 14331 | Planned | Planned Interruption | CONNECT HV JUMPERS AT POLE 908713 TO LIVEN NEW HV CABLE TO MANGAWHAI CENTRAL CB1092
|  | F-8155-A | North River |  | Ruakaka CB7 | 2024-12-07 21:09 | 45633.8809 | 2024-12-08 00:44 | 45634.0308 | 0.68057 | 0.02136 | 1376 | 43841 | Unplanned | Defective Equipment | F 4104345 / FP 388713 - Lines clashed/twisted together. Cleared and relivened
|  | F-8158-A | King Road |  | Mangawhai North CB2 | 2024-12-07 21:38 | 45633.9014 | 2024-12-08 07:31 | 45634.3132 | 1.1569 | 0.013599 | 876 | 74525 | Unplanned | Third Party Interference | Car vs Pole - F 4104358 / FP 388714
|  | O-4993-B | Fert. Works |  | Kioreroa CB6 | 2024-12-08 12:01 | 45634.5007 | 2024-12-08 13:10 | 45634.5486 | 0.035347 | 0.00051228 | 33 | 2277 | Planned | Planned Interruption | Replacing Switch 9045
|  | O-4801-B | Hakaru |  | Kaiwaka CB1032 | 2024-12-09 09:06 | 45635.3792 | 2024-12-09 12:23 | 45635.5161 | 0.012233 | 6.2094e-05 | 4 | 788 | Planned | Planned Interruption | Replace conductor between poles 45962 and 45970
|  | F-8167-A | Bickerstaff |  | Maungaturoto CB2 | 2024-12-09 10:06 | 45635.4211 | 2024-12-09 10:24 | 45635.4335 | 0.20272 | 0.012062 | 777 | 13059 | Unplanned | Unknown | No FPIs available. Closed after 15min
|  | F-8173-A | Jordan Valley |  | Hikurangi CB1102 | 2024-12-10 07:40 | 45636.3194 | 2024-12-10 12:45 | 45636.5311 | 0.20758 | 0.0074048 | 477 | 13372 | Unplanned | Wildlife | 388765/ HV Lines Down at poles 35013 & 35016 caused by ducks
|  | O-16195-A |  |  |  | 2024-12-10 09:04 | 45636.3778 | 2024-12-10 14:55 | 45636.6215 | 0.11987 | 0.00034152 | 22 | 7722 | Planned | Planned Interruption | Replace11 KV cross arms and install B11 pole midspan to gain correct clearance.
|  | O-4891-B | Tangaihi |  | Ruawai CB1032 | 2024-12-10 09:32 | 45636.3972 | 2024-12-10 13:19 | 45636.5549 | 0.021143 | 9.3142e-05 | 6 | 1362 | Planned | Planned Interruption | Cut vegetation from 3092 to EOL
|  | F-133-B | Te Kopuru |  | Dargaville CB2 | 2024-12-10 15:13 | 45636.634 | 2024-12-10 16:23 | 45636.6826 | 0.072806 | 0.0010401 | 67 | 4690 | Unplanned | Defective Equipment | 388779 / Isolate HV to repair broken binders at pole 14497.
|  | O-4804-B | Ararua |  | Mareretu CB2 | 2024-12-11 09:09 | 45637.3812 | 2024-12-11 14:04 | 45637.5861 | 0.46253 | 0.0015679 | 101 | 29795 | Planned | Planned Interruption | Reconductor 11kV lines from H Structure Pole 48027 - 48028 to EOL
|  | O-15487-A | North River |  | Ruakaka CB7 | 2024-12-11 09:28 | 45637.3944 | 2024-12-11 13:09 | 45637.5479 | 0.092629 | 0.00041914 | 27 | 5967 | Planned | Planned Interruption | Replace 13 cross arms and 6 span of conductor. Replace transformer @ Dsub RB146
|  | O-16450-A | Parua Bay |  | Parua Bay CB2 | 2024-12-11 10:03 | 45637.4187 | 2024-12-11 11:43 | 45637.4882 | 0.0015524 | 1.5524e-05 | 1 | 100 | Planned | Planned Interruption | Transformer Upgrade
|  | O-4897-B | Hakaru |  | Kaiwaka CB1032 | 2024-12-12 09:01 | 45638.3758 | 2024-12-12 12:05 | 45638.5033 | 0.01141 | 6.2094e-05 | 4 | 735 | Planned | Planned Interruption | conductor replacement
|  | O-4951-B | Onoke |  | Kamo CB8 | 2024-12-12 09:03 | 45638.3772 | 2024-12-12 12:25 | 45638.5174 | 0.28199 | 0.0013971 | 90 | 18165 | Planned | Planned Interruption | Cut vegetation around 11kv lines from pole #908963 to pole #54293
|  | O-4966-B | Access Rd |  | Ruawai CB1022 | 2024-12-12 09:33 | 45638.3978 | 2024-12-12 13:56 | 45638.5808 | 0.14727 | 0.00055885 | 36 | 9487 | Planned | Planned Interruption | Replace pole #39801 to mitigate road crossing height issue.
|  | F-8188-A | Paranui |  | Tikipunga CB6 | 2024-12-12 22:22 | 45638.9319 | 2024-12-12 23:07 | 45638.9632 | 0.0034928 | 7.7618e-05 | 5 | 225 | Unplanned | Unknown | 388852 / 2 x HV fuses blown causing flames on HV fuses. No obvious cause found. BTN
|  | O-5011-B | Kamo Town |  | Kamo CB7 | 2024-12-13 09:02 | 45639.3764 | 2024-12-13 13:47 | 45639.5743 | 0.49109 | 0.0017231 | 111 | 31635 | Planned | Planned Interruption | New TX KK169 to be added at Pole 30986
|  | O-4957-B | Onoke |  | Kamo CB8 | 2024-12-13 09:05 | 45639.3785 | 2024-12-13 13:39 | 45639.5687 | 0.063802 | 0.00023285 | 15 | 4110 | Planned | Planned Interruption | HV crossarms and hardware replacement
|  | O-4954-B | Hakaru |  | Kaiwaka CB1032 | 2024-12-13 09:09 | 45639.3812 | 2024-12-13 11:15 | 45639.4688 | 0.023472 | 0.00018628 | 12 | 1512 | Planned | Planned Interruption | Network Maintenance- Replace pole 11952
|  | O-4933-B |  |  |  | 2024-12-13 09:42 | 45639.4042 | 2024-12-13 16:34 | 45639.6905 | 1.631 | 0.0058058 | 374 | 105065 | Planned | Planned Interruption | Liven cable SW10167 to pole 312410 Liven new Tx K476-LS ** Phase out in correct, remedial work required.
|  | F-8212-A | Coast |  | Dargaville CB6 | 2024-12-13 18:21 | 45639.7645 | 2024-12-14 03:13 | 45640.134 | 0.18394 | 0.00076066 | 49 | 11849 | Unplanned | Defective Equipment | 388893 / Isolate & Repair broken 25mm XLPE cable at Links 3094
|  | F-8218-A | Taipuha |  | Mareretu CB1 | 2024-12-14 07:21 | 45640.3065 | 2024-12-14 14:42 | 45640.6125 | 0.26815 | 0.0036636 | 236 | 17274 | Unplanned | Defective Equipment | 388895/ HV Line down (Center Phase) between pole 34465 & 34466. Deterioration on cable
|  | F-8224-A | Marua |  | Hikurangi CB1022 | 2024-12-14 17:46 | 45640.7403 | 2024-12-14 19:27 | 45640.8104 | 0.0015679 | 1.5524e-05 | 1 | 101 | Unplanned | Defective Equipment | FP 388901 - Found fuse link corroded. Replaced.
|  | F-8227-A | Puwera |  | Maungatapere CB7 | 2024-12-15 12:43 | 45641.5299 | 2024-12-15 12:45 | 45641.5312 | 3.1047e-05 | 1.5524e-05 | 1 | 2 | Unplanned | Defective Equipment | 388904/ x2 blown HV fuses (Undersized), Opened remaining HV fuse to check size & Close
|  | F-8239-A | Maunu Mountain |  | Maungatapere CB1 | 2024-12-16 04:41 | 45642.1951 | 2024-12-16 05:36 | 45642.2333 | 0.16084 | 0.0041293 | 532 | 10538 | Unplanned | Wildlife | FP 388910 E/F - Possum in lines at Pole 60782
|  | O-5059-B | Hakaru |  | Kaiwaka CB1032 | 2024-12-16 09:02 | 45642.3766 | 2024-12-16 13:57 | 45642.5814 | 0.018318 | 6.2094e-05 | 4 | 1180 | Planned | Planned Interruption | Replace 11kV conductor between poles 327439 and 45976 (These poles are being replaced on 06/11 and will have new numbers)
|  | O-5050-B | North River |  | Ruakaka CB7 | 2024-12-16 10:05 | 45642.4204 | 2024-12-16 12:22 | 45642.5154 | 0.14218 | 0.0010401 | 67 | 9159 | Planned | Planned Interruption | Replace Pole 40898
|  | F-8254-A | ToeToe Rd |  | Kioreroa CB7 | 2024-12-16 16:21 | 45642.6813 | 2024-12-16 20:05 | 45642.8368 | 0.57611 | 0.010929 | 704 | 37112 | Unplanned | Defective Equipment | FP 388941 unknown fault betwn Sw 4385 & 929. Left switching abnormal (Sw 929 open), fault found later on F-8263-A
|  | O-5026-B | Ararua |  | Mareretu CB2 | 2024-12-17 09:02 | 45643.3764 | 2024-12-17 11:36 | 45643.4833 | 0.73632 | 0.0047813 | 308 | 47432 | Planned | Planned Interruption | Upgrading SW2132 to automated switch
|  | O-15517-A | Taipuha |  | Mareretu CB1 | 2024-12-17 09:05 | 45643.3785 | 2024-12-17 11:59 | 45643.4993 | 0.045919 | 0.0002639 | 17 | 2958 | Planned | Planned Interruption | Replace HV crossarms
|  | O-5056-B | Wairere |  | Mareretu CB5 | 2024-12-17 09:35 | 45643.3993 | 2024-12-17 13:44 | 45643.5722 | 0.79627 | 0.0031979 | 206 | 51294 | Planned | Planned Interruption | Replace pole 23782 with B11m type
|  | F-8260-A | Langs Beach |  | Mangawhai North CB3 | 2024-12-17 13:46 | 45643.5734 | 2024-12-17 14:02 | 45643.5848 | 0.20502 | 0.012388 | 798 | 13207 | Unplanned | Unknown | AB Overcurrent trip
|  | F-8263-A | ToeToe Rd |  | Kioreroa CB7 | 2024-12-17 15:26 | 45643.6428 | 2024-12-17 17:46 | 45643.7403 | 0.1028 | 0.0020802 | 134 | 6622 | Unplanned | Defective Equipment | FP388976 - Jumper on crossarm @ pole 30947
|  | F-8266-A | Titoki |  | Poroti CB1032 | 2024-12-17 23:44 | 45643.9887 | 2024-12-17 23:59 | 45643.9991 | 0.044879 | 0.0047347 | 305 | 2891 | Unplanned | Unknown | Sw 8191 indicating EF.
|  | O-5062-B | 2nd Ave |  | Alexander St CB3 | 2024-12-18 09:02 | 45644.3764 | 2024-12-18 15:28 | 45644.6444 | 0.66512 | 0.0017231 | 111 | 42846 | Planned | Planned Interruption | Install new transformer WC473
|  | O-16498-A | Tangowahine |  | Dargaville CB8 | 2024-12-18 09:04 | 45644.3781 | 2024-12-18 15:36 | 45644.6499 | 0.54682 | 0.0013971 | 90 | 35225 | Planned | Planned Interruption | Remove links 3044. - (Links 10200 installed previoulsy NAR 6153) Replace links 3045 with links 10218
|  | F-8275-A | Tangaihi |  | Ruawai CB1032 | 2024-12-18 15:02 | 45644.6266 | 2024-12-18 17:45 | 45644.7399 | 0.70521 | 0.0058058 | 374 | 45428 | Unplanned | Human Error | Remedials for S-2408-A / Isolate & carry out remedials at pole 312410 to fix phase out issue.
|  | F-8278-A | Whangarei Heads |  | Parua Bay CB3 | 2024-12-19 07:06 | 45645.2958 | 2024-12-19 13:25 | 45645.5592 | 1.3026 | 0.012388 | 798 | 83914 | Unplanned | Third Party Interference | 389000 / A & B Phase OC. Large Drone Vs Lines Craig Road causing line down. Bad access resulting in longer outage.
|  | O-5065-B | Hotel |  | Poroti CB1052 | 2024-12-19 09:02 | 45645.3764 | 2024-12-19 14:12 | 45645.5916 | 0.21646 | 0.00069856 | 45 | 13944 | Planned | Planned Interruption | TX W166 upgrade to 100kVA
|  | O-5077-B | Ararua |  | Mareretu CB2 | 2024-12-19 09:04 | 45645.3778 | 2024-12-19 14:53 | 45645.6201 | 1.1106 | 0.0031823 | 205 | 71545 | Planned | Planned Interruption | Replace OH conductor
|  | F-8281-A | Langs Beach |  | Mangawhai North CB3 | 2024-12-19 09:46 | 45645.4071 | 2024-12-19 10:02 | 45645.4181 | 0.19552 | 0.012388 | 798 | 12595 | Unplanned | Unknown | 389010 / Trip B & C Phase OC. FPIs at Sw 5482 Activated. L2 & L3.
|  | F-142-B | Te Kopuru |  | Dargaville CB2 | 2024-12-19 12:22 | 45645.5153 | 2024-12-19 13:01 | 45645.5424 | 0.14591 | 0.0037412 | 241 | 9399 | Unplanned | Defective Equipment | 388797 / Isolate to repair broken X arm at pole 14358.
|  | F-8284-A | Titoki |  | Poroti CB1032 | 2024-12-20 09:47 | 45646.4075 | 2024-12-20 13:46 | 45646.5736 | 0.38311 | 0.0047347 | 305 | 24679 | Unplanned | Unknown | FP 389034 - Suspected logging company bringing lines down from loader. Faulty tele switch past fault area.
|  | F-8287-A | Te Kopuru |  | Dargaville CB2 | 2024-12-20 12:13 | 45646.5093 | 2024-12-20 17:54 | 45646.7458 | 0.035409 | 0.00027943 | 18 | 2281 | Unplanned | Defective Equipment | FP 389038 - Replaced faulty 11kV Fuses
|  | F-145-B | Te Kopuru |  | Dargaville CB2 | 2024-12-21 07:39 | 45647.3187 | 2024-12-21 08:32 | 45647.3556 | 0.01481 | 0.00027943 | 18 | 954 | Unplanned | Defective Equipment | FP 389045 - Replaced faulty 11kV Fuses
|  | F-8293-A | Treatment |  | Kioreroa CB2 | 2024-12-23 04:18 | 45649.1789 | 2024-12-23 08:07 | 45649.3382 | 0.72146 | 0.0034928 | 225 | 46475 | Unplanned | Defective Equipment | FP389054/389053 Sw9061 faulty indicatio (appeared to be closed but didn't item8 F8290-a). Fault found later on F-8293-a 2nd trip
|  | O-5122-B |  |  |  | 2024-12-23 10:40 | 45649.4444 | 2024-12-23 10:50 | 45649.4514 | 0.011798 | 0.0011798 | 76 | 760 | Planned | Planned Interruption | Tx WC463 tap change. Late start due to scheduling issue.
|  | F-8302-A | Treatment |  | Kioreroa CB2 | 2024-12-25 15:41 | 45651.6535 | 2024-12-25 20:35 | 45651.8576 | 0.11866 | 0.00040361 | 26 | 7644 | Unplanned | Defective Equipment | FP 389080 - UG HV fault between L9060 & WO199. Generated overnight
|  | F-8308-A | Pataua |  | Parua Bay CB1 | 2024-12-27 10:28 | 45653.4361 | 2024-12-27 11:12 | 45653.4667 | 0.056009 | 0.0012729 | 82 | 3608 | Unplanned | Defective Equipment | FP 389091 - Replace faulty DDOs
|  | F-8311-A | Mata |  | Ruakaka CB3 | 2024-12-27 12:22 | 45653.5155 | 2024-12-27 12:38 | 45653.5261 | 0.065665 | 0.0069701 | 449 | 4230 | Unplanned | Adverse Weather | FPIs Sw 503 AB ph, OC B ph @ RKA sub. Windy conditions.
|  | F-8314-A | Bickerstaff |  | Maungaturoto CB2 | 2024-12-27 12:49 | 45653.5338 | 2024-12-27 13:11 | 45653.5492 | 0.25015 | 0.012062 | 777 | 16114 | Unplanned | Adverse Weather | High Winds most likely cause.
|  | F-8317-A | Matapouri |  | Ngunguru CB1032 | 2024-12-27 13:21 | 45653.556 | 2024-12-27 18:12 | 45653.7583 | 0.7712 | 0.0076066 | 490 | 49679 | Unplanned | Vegetation | F 4117544 / FP 389096 - Trees in lines
|  | F-8320-A | Taipuha |  | Mareretu CB1 | 2024-12-27 13:31 | 45653.5635 | 2024-12-27 19:51 | 45653.8271 | 0.26297 | 0.0036636 | 236 | 16940 | Unplanned | Vegetation | 389102 - Lines down between 34207 & 32561 Bull Rd
|  | F-8323-A | Kaiatea |  | Ngunguru CB1072 | 2024-12-27 13:49 | 45653.5757 | 2024-12-27 18:54 | 45653.7875 | 1.0734 | 0.021174 | 1364 | 69145 | Unplanned | Adverse Weather | FP 389122 - AC FPIs sw 720, light patrol. Field staff advised lines swinging heavily in wind.
|  | F-8326-A | Thelma Road |  | Mangawhai North CB4 | 2024-12-27 14:27 | 45653.6022 | 2024-12-27 19:42 | 45653.8208 | 0.86654 | 0.013614 | 877 | 55821 | Unplanned | Defective Equipment | 389114 - Lines down - possibly due to clashing
|  | F-8329-A | North River |  | Ruakaka CB7 | 2024-12-27 14:37 | 45653.6089 | 2024-12-27 20:05 | 45653.837 | 5.0242 | 0.037303 | 2403 | 323647 | Unplanned | Defective Equipment | 389104 - replaceed 2 xampacts at pole 337557
|  | F-8332-A | Whakapara |  | Hikurangi CB1112 | 2024-12-27 14:40 | 45653.6114 | 2024-12-27 17:06 | 45653.7122 | 0.88152 | 0.0060697 | 391 | 56786 | Unplanned | Adverse Weather | F 4117622 / FP 389117 - FENZ reported low lines. Field staff found Chorus lines.
|  | F-8341-A | Tamaterau |  | Onerahi CB7 | 2024-12-27 21:16 | 45653.8861 | 2024-12-28 00:23 | 45654.016 | 0.15676 | 0.00083828 | 54 | 10098 | Unplanned | Defective Equipment | FP 389129 - Repair 11kV cable termination
|  | F-8344-A | North Kaiwaka |  | Kaiwaka CB1022 | 2024-12-27 22:25 | 45653.934 | 2024-12-27 23:55 | 45653.9965 | 0.055652 | 0.0012574 | 81 | 3585 | Unplanned | Defective Equipment | 389125 Jumper off on the line side of Links 419
|  | F-8362-A | North Dargaville |  | Dargaville CB1 | 2024-12-30 15:38 | 45656.6511 | 2024-12-30 21:29 | 45656.8951 | 0.20622 | 0.0041603 | 268 | 13284 | Unplanned | Defective Equipment | FP389164/ Replaced Faulty Tx - HV Bushing Fail
|  | F-8359-A | Kaiatea |  | Ngunguru CB1072 | 2024-12-30 15:38 | 45656.6511 | 2024-12-30 19:53 | 45656.8286 | 0.96099 | 0.010587 | 682 | 61905 | Unplanned | Defective Equipment | FP389163/ HV Lines Clashing between Spur & Main Line.
|  | F-8374-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2025-01-02 22:15 | 45659.9272 | 2025-01-02 22:45 | 45659.9477 | 2.6803 | 0.10559 | 6805 | 172732 | Unplanned | Lightning | FP 389184. CB 1222 MTO & CB 72 MTON Tripped. Patrolled Relivened - further daylight patrol required, fault found on F-8377-A
|  | F-8377-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2025-01-03 14:47 | 45660.6157 | 2025-01-03 16:23 | 45660.6825 | 6.0972 | 0.073862 | 4760 | 392931 | Unplanned | Lightning | 389184 / Isolate 33kV to replace blown insulator on pole 17708. Most probable cause from on site staff said lightning stike.
|  | F-8398-A | Taipuha |  | Mareretu CB1 | 2025-01-06 14:56 | 45663.622 | 2025-01-06 14:57 | 45663.6228 | 0.0075569 | 0.0070914 | 457 | 487 | Unplanned | Unknown | Trip EF.FPI @ sw364 Phase A & N
|  | O-5080-B | Coast |  | Dargaville CB6 | 2025-01-07 09:02 | 45664.3762 | 2025-01-07 11:12 | 45664.4666 | 0.056529 | 0.00043448 | 28 | 3643 | Planned | Planned Interruption | Repair guy wire / replace DOFs L133
|  | O-5074-B | Taipuha |  | Mareretu CB1 | 2025-01-07 09:02 | 45664.3764 | 2025-01-07 12:18 | 45664.5125 | 0.1764 | 0.0009 | 58 | 11368 | Planned | Planned Interruption | HV crossarm replacement
|  | O-5068-B |  |  |  | 2025-01-07 09:14 | 45664.385 | 2025-01-07 13:45 | 45664.573 | 0.1764 | 0.00065172 | 42 | 11368 | Planned | Planned Interruption | HV cross-arm replacement
|  | O-5320-B | King Road |  | Mangawhai North CB2 | 2025-01-07 13:18 | 45664.5542 | 2025-01-07 14:08 | 45664.5889 | 0.010862 | 0.00021724 | 14 | 700 | Planned | Planned Interruption | Inspect HV bushing
|  | O-5095-B | Kokopu |  | Poroti CB1022 | 2025-01-08 09:04 | 45665.3778 | 2025-01-08 13:54 | 45665.5792 | 0.198 | 0.00068276 | 44 | 12760 | Planned | Planned Interruption | Replace various crossarms and pole 12793
|  | O-5092-B | North River |  | Ruakaka CB7 | 2025-01-08 09:05 | 45665.3785 | 2025-01-08 14:10 | 45665.5903 | 0.5348 | 0.0017534 | 113 | 34465 | Planned | Planned Interruption | Install new transformer RB336, poles and aerial conductor
|  | O-5191-B | Turiwiri |  | Dargaville CB9 | 2025-01-08 10:45 | 45665.4479 | 2025-01-08 11:37 | 45665.484 | 0.0032276 | 6.2069e-05 | 4 | 208 | Planned | Planned Interruption | Drop redundant lines away from pole #21880 remove Tx J210 & J241 from serivce
|  | F-8434-A | Jordan Valley |  | Hikurangi CB1102 | 2025-01-08 16:38 | 45665.6931 | 2025-01-08 22:27 | 45665.9354 | 0.45928 | 0.019629 | 1265 | 29598 | Unplanned | Defective Equipment | 389312/Broken Line down from Ampac connection pole 35863.
|  | O-5104-B | Otangarei |  | Tikipunga CB7 | 2025-01-09 09:03 | 45666.3771 | 2025-01-09 12:16 | 45666.5111 | 0.29649 | 0.0015362 | 99 | 19107 | Planned | Planned Interruption | Replace LV Link Pillar replacement
|  | O-5101-B | Titoki |  | Poroti CB1032 | 2025-01-09 09:16 | 45666.3862 | 2025-01-09 14:28 | 45666.6031 | 0.63012 | 0.0020172 | 130 | 40608 | Planned | Planned Interruption | Tree clearing work
|  | O-5215-B | Whatatiri |  | Maungatapere CB8 | 2025-01-09 09:23 | 45666.3911 | 2025-01-09 14:25 | 45666.6006 | 0.47262 | 0.0015672 | 101 | 30458 | Planned | Planned Interruption | Replant and straighten various poles
|  | O-5089-B | Jordan Valley |  | Hikurangi CB1102 | 2025-01-09 09:34 | 45666.3986 | 2025-01-09 12:41 | 45666.5285 | 0.058034 | 0.00031034 | 20 | 3740 | Planned | Planned Interruption | TX structure upgrade
|  | F-8443-A | Taipuha |  | Mareretu CB1 | 2025-01-09 20:16 | 45666.8444 | 2025-01-10 14:11 | 45667.591 | 0.016681 | 1.5517e-05 | 1 | 1075 | Unplanned | Defective Equipment | FP 389357 - Isolate Tx X387, cable to be repaired. 1 unused water pump
|  | O-5164-B | Kiripaka Rd |  | Tikipunga CB8 | 2025-01-10 09:04 | 45667.3778 | 2025-01-10 14:13 | 45667.5924 | 0.12946 | 0.00041897 | 27 | 8343 | Planned | Planned Interruption | Switch 704 decommissioned, switch 10170 being installed
|  | O-5110-B | Mata |  | Ruakaka CB3 | 2025-01-10 09:33 | 45667.3979 | 2025-01-10 11:27 | 45667.4771 | 0.0070759 | 6.2069e-05 | 4 | 456 | Planned | Planned Interruption | Bolt down transformer RO269
|  | F-8449-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-01-11 11:10 | 45668.4654 | 2025-01-11 11:26 | 45668.4761 | 0.12366 | 0.0079603 | 513 | 7969 | Unplanned | Unknown | BC ph FPIs @ Sw 320. Sw 320 tele control faulty. Reclosed after 15.
|  | F-8455-A | Commercial |  | Mangawhai Central | 2025-01-13 00:57 | 45670.0396 | 2025-01-13 01:13 | 45670.0509 | 0.12507 | 0.013609 | 877 | 8060 | Unplanned | Unknown | A, B, C phase beyond Sw 4270
|  | O-5116-B | Rewa Rewa Rd |  | Whangarei South CB1082 | 2025-01-13 09:05 | 45670.3785 | 2025-01-13 14:43 | 45670.6132 | 0.30944 | 0.00091552 | 59 | 19942 | Planned | Planned Interruption | Link Pillar replacement - HV isolated to access LV
|  | O-5206-B | Kokopu |  | Poroti CB1022 | 2025-01-13 09:15 | 45670.3856 | 2025-01-13 13:17 | 45670.5537 | 0.61597 | 0.0025448 | 164 | 39696 | Planned | Planned Interruption | Replace pole to increase ground clearance, replace crossarms and redo connections
|  | O-5218-B | Langs Beach |  | Mangawhai North CB3 | 2025-01-13 10:07 | 45670.4215 | 2025-01-13 13:29 | 45670.5618 | 0.068959 | 0.00034138 | 22 | 4444 | Planned | Planned Interruption | New TX RR354 added to network
|  | F-8461-A | Titoki |  | Poroti CB1032 | 2025-01-13 10:48 | 45670.4501 | 2025-01-13 13:14 | 45670.5514 | 0.27313 | 0.0029328 | 189 | 17602 | Unplanned | Defective Equipment | Lines down - FP389430
|  | O-5221-B | North Dargaville |  | Dargaville CB1 | 2025-01-13 10:55 | 45670.4549 | 2025-01-13 12:42 | 45670.5292 | 0.076376 | 0.00071379 | 46 | 4922 | Planned | Planned Interruption | Replace 3138KL with NGK 630A type
|  | F-8467-A | Tangaihi |  | Ruawai CB1032 | 2025-01-13 15:02 | 45670.6264 | 2025-01-13 15:15 | 45670.6354 | 0.0012103 | 9.3103e-05 | 6 | 78 | Unplanned | Vegetation | FP 389439 - tree branch in OH lines
|  | O-15898-A | Taipuha |  | Mareretu CB1 | 2025-01-14 09:04 | 45671.3778 | 2025-01-14 12:26 | 45671.5181 | 0.024983 | 0.00012414 | 8 | 1610 | Planned | Planned Interruption | Replace pole 34567 and replace cross arms at various poles
|  | O-5119-B | Ararua |  | Mareretu CB2 | 2025-01-14 09:05 | 45671.3785 | 2025-01-14 14:47 | 45671.616 | 0.57314 | 0.0016759 | 108 | 36936 | Planned | Planned Interruption | Upgrade TX E208 and replace 2 x poles
|  | O-5125-B | Te Kopuru |  | Dargaville CB2 | 2025-01-14 09:33 | 45671.3979 | 2025-01-14 13:12 | 45671.55 | 0.1937 | 0.00088448 | 57 | 12483 | Planned | Planned Interruption | Tree clearing work
|  | F-8473-A | Maungakaramea |  | Maungatapere CB3 | 2025-01-14 21:53 | 45671.9118 | 2025-01-15 01:03 | 45672.0437 | 0.023586 | 0.00012414 | 8 | 1520 | Unplanned | Defective Equipment | 389475 / Isolate HV to replace broken pole 53770
|  | O-15127-A | Turiwiri |  | Dargaville CB9 | 2025-01-15 09:03 | 45672.3771 | 2025-01-15 14:25 | 45672.6007 | 0.094934 | 0.00029483 | 19 | 6118 | Planned | Planned Interruption | Replace HV and LV cross arms
|  | O-5203-B | Thelma Road |  | Mangawhai North CB4 | 2025-01-15 09:06 | 45672.3792 | 2025-01-15 11:07 | 45672.4632 | 0.026286 | 0.00021724 | 14 | 1694 | Planned | Planned Interruption | DOF MC288 being replaced
|  | O-5128-B |  |  |  | 2025-01-15 09:23 | 45672.391 | 2025-01-15 14:34 | 45672.6069 | 0.35078 | 0.0011483 | 74 | 22606 | Planned | Planned Interruption | Isolated for LV repair works
|  | F-8479-A | Ruatangata |  | Kamo CB6 | 2025-01-15 11:15 | 45672.4688 | 2025-01-15 13:28 | 45672.5611 | 0.0041276 | 3.1034e-05 | 2 | 266 | Unplanned | Defective Equipment | 389484 Broken DOFs to be replaced
|  | F-8488-A | Ararua |  | Mareretu CB2 | 2025-01-16 08:12 | 45673.3418 | 2025-01-16 17:51 | 45673.7438 | 1.1468 | 0.026348 | 1698 | 73904 | Unplanned | Third Party Interference | Agricultural Drone in lines. Crossarm broken, pole cracked. FP 389517
|  | O-15928-A | Taipuha |  | Mareretu CB1 | 2025-01-16 09:03 | 45673.3773 | 2025-01-16 12:57 | 45673.5397 | 0.31947 | 0.0013655 | 88 | 20588 | Planned | Planned Interruption | Replace cross arms
|  | O-5155-B | Ararua |  | Mareretu CB2 | 2025-01-16 09:10 | 45673.3819 | 2025-01-16 12:40 | 45673.5278 | 0.66802 | 0.003181 | 205 | 43050 | Planned | Planned Interruption | Replace conductor between poles 911547 and 406935
|  | O-16267-A | Paranui |  | Tikipunga CB6 | 2025-01-16 09:11 | 45673.3826 | 2025-01-16 11:34 | 45673.4819 | 0.013314 | 9.3103e-05 | 6 | 858 | Planned | Planned Interruption | Level D-sub KT360
|  | O-5224-B | Whatatiri |  | Maungatapere CB8 | 2025-01-16 09:32 | 45673.3972 | 2025-01-16 14:24 | 45673.6 | 0.43045 | 0.0014741 | 95 | 27740 | Planned | Planned Interruption | Tree clearing work
|  | O-5230-B | Matapouri |  | Ngunguru CB1032 | 2025-01-16 10:10 | 45673.4236 | 2025-01-16 12:29 | 45673.5201 | 0.0064707 | 4.6552e-05 | 3 | 417 | Planned | Planned Interruption | Level TX NT201
|  | F-8497-A | North Dargaville |  | Dargaville CB1 | 2025-01-16 20:32 | 45673.8552 | 2025-01-17 12:21 | 45674.5146 | 0.79319 | 0.02101 | 1354 | 51117 | Unplanned | Defective Equipment | 389542 Lines down reported at 119 Waikara Road
|  | O-5140-B | Turiwiri |  | Dargaville CB9 | 2025-01-17 09:06 | 45674.3792 | 2025-01-17 15:08 | 45674.6306 | 0.1346 | 0.00037241 | 24 | 8674 | Planned | Planned Interruption | Crossarms replacement
|  | O-5407-B | Otonga |  | Hikurangi CB1032 | 2025-01-17 09:31 | 45674.3965 | 2025-01-17 13:33 | 45674.5646 | 0.34304 | 0.0015983 | 103 | 22107 | Planned | Planned Interruption | Replace damaged HV cable riser on pole #302523 and re configure cross arm to install crucifix above transformer
|  | F-8512-A | Coast |  | Dargaville CB6 | 2025-01-19 10:43 | 45676.4465 | 2025-01-19 10:58 | 45676.4572 | 0.0423 | 0.0027465 | 177 | 2726 | Unplanned | Unknown | Nil / Trip A & B Phase. 15 Min Close & BTN
|  | F-8515-A | Kiripaka Rd |  | Tikipunga CB8 | 2025-01-19 13:05 | 45676.5454 | 2025-01-19 14:06 | 45676.5875 | 0.0028241 | 4.6552e-05 | 3 | 182 | Unplanned | Unknown | 389575 / 2 x HV fuses blown wth no obvious cause. All BTN
|  | F-8521-A | Tutukaka Block |  | Ngunguru CB1082 | 2025-01-19 22:53 | 45676.9535 | 2025-01-20 03:19 | 45677.1385 | 1.5277 | 0.010288 | 663 | 98451 | Unplanned | Lightning | FP - 389582 Blown LA at fuses NP181
|  | F-8524-A | Coast |  | Dargaville CB6 | 2025-01-20 01:16 | 45677.0528 | 2025-01-20 02:04 | 45677.0861 | 0.037241 | 0.00077586 | 50 | 2400 | Unplanned | Vegetation | 389580 Trees blowing in the HV - started fire
|  | F-8527-A | Titoki |  | Poroti CB1032 | 2025-01-21 03:09 | 45678.1312 | 2025-01-21 10:24 | 45678.4333 | 0.38337 | 0.011964 | 771 | 24706 | Unplanned | Defective Equipment | FP 389629 - Replace faulty tx
|  | F-8533-A | North River |  | Ruakaka CB7 | 2025-01-21 03:47 | 45678.1576 | 2025-01-21 11:37 | 45678.484 | 0.89795 | 0.0076345 | 492 | 57868 | Unplanned | Vegetation | 389632 Trees in lines at RB120
|  | F-8536-A | Tamaterau |  | Onerahi CB7 | 2025-01-21 04:56 | 45678.2055 | 2025-01-21 04:58 | 45678.2068 | 0.016867 | 0.0087207 | 562 | 1087 | Unplanned | Adverse Weather | A & B O/C - Trip and close.
|  | F-8539-A | Kokopu |  | Poroti CB1022 | 2025-01-21 05:02 | 45678.2096 | 2025-01-21 11:17 | 45678.4701 | 1.2633 | 0.011002 | 709 | 81412 | Unplanned | Defective Equipment | FP 389637 - Repair lines down @ pole 315224
|  | F-8542-A | Whatatiri |  | Maungatapere CB8 | 2025-01-21 06:16 | 45678.2608 | 2025-01-21 06:31 | 45678.2715 | 0.13908 | 0.0095431 | 615 | 8963 | Unplanned | Adverse Weather | Fault is beyond SW 843 - closed after 15 min
|  | F-8545-A | Whakapara |  | Hikurangi CB1112 | 2025-01-21 07:22 | 45678.3069 | 2025-01-21 07:54 | 45678.3295 | 0.39934 | 0.01696 | 1093 | 25735 | Unplanned | Adverse Weather | Trip and close >15. FPIs Sw 663 ABC
|  | F-8548-A | Paranui |  | Tikipunga CB6 | 2025-01-21 09:05 | 45678.3783 | 2025-01-21 09:06 | 45678.379 | 0.012134 | 0.011374 | 733 | 782 | Unplanned | Unknown | Tripped & Closed
|  | O-5233-B | Bickerstaff |  | Maungaturoto CB2 | 2025-01-21 09:07 | 45678.3799 | 2025-01-23 13:15 | 45680.5521 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Raise RMU
|  | O-5143-B | Whatatiri |  | Maungatapere CB8 | 2025-01-21 10:36 | 45678.4414 | 2025-01-21 14:36 | 45678.6083 | 0.73085 | 0.0030414 | 196 | 47099 | Planned | Planned Interruption | Upgrade switch 849 to automated switch
|  | F-8554-A | Paparoa |  | Mareretu CB6 | 2025-01-21 11:02 | 45678.46 | 2025-01-21 16:30 | 45678.6875 | 0.58039 | 0.0091862 | 592 | 37403 | Unplanned | Vegetation | FP 389669 - LV lines down from tree
|  | F-8557-A | Puwera |  | Maungatapere CB7 | 2025-01-21 11:09 | 45678.4645 | 2025-01-21 17:17 | 45678.7201 | 0.32901 | 0.0041897 | 270 | 21203 | Unplanned | Defective Equipment | 389674 Lines down near TX X353
|  | F-8569-A | Taipuha |  | Mareretu CB1 | 2025-01-21 14:28 | 45678.6025 | 2025-01-21 17:23 | 45678.7243 | 0.081652 | 0.00135 | 87 | 5262 | Unplanned | Defective Equipment | 389685 HV lines down at pole 34207
|  | O-5260-B | North River |  | Ruakaka CB7 | 2025-01-22 07:02 | 45679.2931 | 2025-01-22 14:06 | 45679.5875 | 0.7445 | 0.0066259 | 427 | 47979 | Planned | Planned Interruption | Install new OH switch to replace links 542
|  | O-5158-B | Tangowahine |  | Dargaville CB8 | 2025-01-22 09:05 | 45679.3785 | 2025-01-22 15:27 | 45679.6438 | 0.065203 | 0.00017069 | 11 | 4202 | Planned | Planned Interruption | Replace poles and 11kV conductor
|  | O-16222-A | Titoki |  | Poroti CB1032 | 2025-01-22 09:06 | 45679.3792 | 2025-01-22 15:12 | 45679.6333 | 0.60405 | 0.0017069 | 110 | 38928 | Planned | Planned Interruption | Replace cross arms, Connections and HV links 792
|  | O-5251-B | Marsden Pt |  | Ruakaka CB1 | 2025-01-22 09:22 | 45679.3903 | 2025-01-22 11:43 | 45679.4882 | 0.11377 | 0.0008069 | 52 | 7332 | Planned | Planned Interruption | Replace Voltage indicators
|  | O-5227-B | Langs Beach |  | Mangawhai North CB3 | 2025-01-22 09:37 | 45679.4007 | 2025-01-22 12:19 | 45679.5132 | 0.062845 | 0.00038793 | 25 | 4050 | Planned | Planned Interruption | Install new TX RR356
|  | O-5302-B | Paparoa |  | Mareretu CB6 | 2025-01-23 09:07 | 45680.3798 | 2025-01-23 14:37 | 45680.6088 | 0.87395 | 0.002669 | 172 | 56321 | Planned | Planned Interruption | Replace HV poles and cross arms Refurbish Dsubs A150 and A131 and replace HV and LV cross arms at various sites
|  | O-5416-B | North Dargaville |  | Dargaville CB1 | 2025-01-23 09:19 | 45680.3882 | 2025-01-23 11:52 | 45680.4944 | 0.018993 | 0.00012414 | 8 | 1224 | Planned | Planned Interruption | Remove 11KV line From Pole 27184 to Pole 27191 including TX M516
|  | O-5275-B |  |  |  | 2025-01-24 09:01 | 45681.3757 | 2025-01-24 13:51 | 45681.5773 | 1.2436 | 0.0042828 | 276 | 80141 | Planned | Planned Interruption | Replacing pole and cross arms, 10294,52339,10317
|  | O-5209-B | Langs Beach |  | Mangawhai North CB3 | 2025-01-24 09:04 | 45681.3778 | 2025-01-24 14:32 | 45681.6056 | 0.076345 | 0.00023276 | 15 | 4920 | Planned | Planned Interruption | Replace transformer RR221 with a 300kva with existing label RR221
|  | O-5287-B |  |  |  | 2025-01-24 09:18 | 45681.3875 | 2025-01-24 14:13 | 45681.5924 | 0.49438 | 0.0016759 | 108 | 31860 | Planned | Planned Interruption | Improvements in Supply Quality - Replace Pole 48701 and Pole 48513. Install 3 ph 50kva transformer at pole 48513 and label E425
|  | F-8599-A | Matapouri |  | Ngunguru CB1032 | 2025-01-24 09:31 | 45681.3968 | 2025-01-24 11:26 | 45681.4764 | 0.3685 | 0.012305 | 793 | 23748 | Unplanned | Third Party Interference | 389807 Tree felled into line
|  | O-17401-A | Matapouri |  | Ngunguru CB1032 | 2025-01-24 14:07 | 45681.5882 | 2025-01-25 10:26 | 45682.4347 | 0.11131 | 0.00069828 | 45 | 7173 | Unplanned | Defective Equipment | 389815 Generator connected to Tx NT131 @1730hrs Replaced 3x HV fuse bases F7205
|  | F-8614-A | Matapouri |  | Ngunguru CB1032 | 2025-01-26 02:19 | 45683.0968 | 2025-01-26 02:34 | 45683.1073 | 0.10583 | 0.01229 | 792 | 6820 | Unplanned | Lightning | Suspected lightning strike
|  | F-8617-A | Langs Beach |  | Mangawhai North CB3 | 2025-01-26 02:50 | 45683.1181 | 2025-01-26 10:29 | 45683.4368 | 5.1949 | 0.012429 | 801 | 334780 | Unplanned | Adverse Weather | 389850 Feeder tripped during weather event,TORNADO Ref: F-8623-a & F-8626-A
|  | F-8623-A | KAI - MWI 33kV |  | Kaiwaka CB52 | 2025-01-26 02:56 | 45683.1219 | 2025-01-28 16:16 | 45685.6778 | 25.0559 | 0.063202 | 4073 | 1614712 | Unplanned | Adverse Weather | 389845 / Tornado Damages Mangawhai Ref: F-8623-a
|  | O-17410-A | Hakaru |  | Kaiwaka CB1032 | 2025-01-26 05:56 | 45683.247 | 2025-01-26 07:24 | 45683.3083 | 0.31377 | 0.0035534 | 229 | 20221 | Unplanned | Other Cause | De-energised for safety due to report of sparking on pole. Inspected, no fault found. (33kV FPIs flashing)
|  | F-8629-A | Tangaihi |  | Ruawai CB1032 | 2025-01-26 08:23 | 45683.3493 | 2025-01-26 11:54 | 45683.4958 | 0.13877 | 0.0014431 | 93 | 8943 | Unplanned | Lightning | 389844 DOFs damaged requiring replacement
|  | F-8632-A | One Tree Point |  | Ruakaka CB6 | 2025-01-26 09:12 | 45683.3833 | 2025-01-26 09:13 | 45683.384 | 0.0066414 | 0.0065328 | 421 | 428 | Unplanned | Unknown | 1 min close
|  | F-8641-A | Bickerstaff |  | Maungaturoto CB2 | 2025-01-26 14:08 | 45683.5887 | 2025-01-26 17:49 | 45683.7421 | 0.59645 | 0.0094655 | 610 | 38438 | Unplanned | Defective Equipment | 389852 Blown jumper at pole 23693
|  | F-8644-A | Tangowahine |  | Dargaville CB8 | 2025-01-27 17:41 | 45684.7368 | 2025-01-27 17:59 | 45684.7496 | 0.037319 | 0.0089845 | 579 | 2405 | Unplanned | Unknown | Trip Overcurrent A B & C. FPIs at Sw 2037 activated. Closed & BTN
|  | F-8647-A | Bickerstaff |  | Maungaturoto CB2 | 2025-01-27 18:54 | 45684.7875 | 2025-01-27 19:08 | 45684.7976 | 0.17505 | 0.012072 | 778 | 11281 | Unplanned | Unknown | OC
|  | F-8650-A | North Kaiwaka |  | Kaiwaka CB1022 | 2025-01-27 21:44 | 45684.9056 | 2025-01-27 21:56 | 45684.9142 | 0.042284 | 0.0033828 | 218 | 2725 | Unplanned | Unknown | O/C
|  | F-8656-A | One Tree Point |  | Ruakaka CB6 | 2025-01-28 07:11 | 45685.2993 | 2025-01-28 07:12 | 45685.3002 | 0.0088138 | 0.0065328 | 421 | 568 | Unplanned | Unknown | Trip B & C Overcurrent. BTN
|  | O-5437-B | Maunu Mountain |  | Maungatapere CB1 | 2025-01-28 09:01 | 45685.3759 | 2025-01-28 10:26 | 45685.4345 | 0.065452 | 0.00077586 | 50 | 4218 | Planned | Planned Interruption | Remove Links 8842KL and replace with jumpers
|  | O-5311-B |  |  |  | 2025-01-28 09:08 | 45685.3806 | 2025-01-28 14:15 | 45685.5938 | 0.061929 | 0.00020172 | 13 | 3991 | Planned | Planned Interruption | Replace x-arms at poles 33629 and 33630 & LV Xarms from B212
|  | O-5308-B | Jordan Valley |  | Hikurangi CB1102 | 2025-01-28 09:39 | 45685.4021 | 2025-01-28 14:51 | 45685.6188 | 0.1985 | 0.00063621 | 41 | 12792 | Planned | Planned Interruption | HV Isolation for safety Replacing LV conductor from KR201
|  | O-5401-B | Taipuha |  | Mareretu CB1 | 2025-01-28 09:52 | 45685.4111 | 2025-01-28 13:17 | 45685.5535 | 0.025448 | 0.00012414 | 8 | 1640 | Planned | Planned Interruption | LV pole and crossarm replacement
|  | F-8665-A | Whakapara |  | Hikurangi CB1112 | 2025-01-28 10:52 | 45685.4527 | 2025-01-28 11:07 | 45685.4633 | 0.19291 | 0.01696 | 1093 | 12432 | Unplanned | Unknown | Fault beyond SW663, closed after 15min, held
|  | O-5425-B | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-01-28 11:30 | 45685.4795 | 2025-01-28 12:34 | 45685.5237 | 0.10168 | 0.0015983 | 103 | 6553 | Planned | Planned Interruption | Remove links 8881KL
|  | F-8668-A | Te Kopuru |  | Dargaville CB2 | 2025-01-29 06:24 | 45686.2667 | 2025-01-29 06:40 | 45686.2777 | 0.1381 | 0.01471 | 948 | 8900 | Unplanned | Unknown | B ph & N fault - Close >15min
|  | O-5392-B | North River |  | Ruakaka CB7 | 2025-01-29 09:00 | 45686.3753 | 2025-01-29 12:41 | 45686.5285 | 0.78738 | 0.003569 | 230 | 50742 | Planned | Planned Interruption | Replace 11kV pole and cross arms, replace one span of 11KV conductor, Refurbish Dsub RB218
|  | O-5329-B | Brynderwyn |  | Maungaturoto CB1 | 2025-01-29 09:22 | 45686.3903 | 2025-01-29 14:43 | 45686.6132 | 0.084678 | 0.00026379 | 17 | 5457 | Planned | Planned Interruption | Replace pole hardware & transformer D387 like for like, from pole 23609 to EOL
|  | O-15934-A | Ararua |  | Mareretu CB2 | 2025-01-30 09:01 | 45687.376 | 2025-01-30 13:47 | 45687.574 | 0.66791 | 0.0023431 | 151 | 43043 | Planned | Planned Interruption | Replace HV & LV cross arms and refurbish various Dsubs
|  | O-4963-B | Kiripaka Rd |  | Tikipunga CB8 | 2025-01-30 09:09 | 45687.3812 | 2025-01-31 15:58 | 45688.6653 | 1.0985 | 0.0022655 | 146 | 70793 | Planned | Planned Interruption | Install new RMU. Post livening issue. Generation used over night. upgrade TX KT162 following day.
|  | O-5332-B | Kiripaka Rd |  | Tikipunga CB8 | 2025-01-31 00:02 | 45688.0014 | 2025-01-31 01:33 | 45688.0646 | 0.30924 | 0.0033983 | 219 | 19929 | Planned | Planned Interruption | Improvements in Supply Quality - INSTALL HV POST ISULATORS TO IMPROVE CLEARANCE BETWEEN 11Kv JUMPERS AND CROSSARMS
|  | O-5434-B | Taipuha |  | Mareretu CB1 | 2025-01-31 09:05 | 45688.3785 | 2025-01-31 13:25 | 45688.559 | 0.076655 | 0.00029483 | 19 | 4940 | Planned | Planned Interruption | Install TX X525
|  | O-5446-B | Ararua |  | Mareretu CB2 | 2025-01-31 09:16 | 45688.3861 | 2025-01-31 16:22 | 45688.6819 | 0.71392 | 0.0016759 | 108 | 46008 | Planned | Planned Interruption | Upgrade LV overhead lines between poles 980606 and 48704. Remove LV overhead lines between poles 909762 and 911799
|  | O-5335-B | Puwera |  | Maungatapere CB7 | 2025-01-31 09:26 | 45688.3932 | 2025-01-31 10:33 | 45688.4394 | 0.019598 | 0.00029483 | 19 | 1263 | Planned | Planned Interruption | Remove links 8049KL
|  | O-5461-B | Taipuha |  | Mareretu CB1 | 2025-01-31 10:47 | 45688.4493 | 2025-01-31 11:50 | 45688.4931 | 0.087983 | 0.0013966 | 90 | 5670 | Planned | Planned Interruption | Urgent Repairs - replace HV arms, LV connections, Straighten pole and replace stay wires
|  | F-8686-A | Waipu |  | Ruakaka CB2 | 2025-02-01 08:22 | 45689.3486 | 2025-02-01 09:04 | 45689.3776 | 0.079594 | 0.001908 | 123 | 5131 | Unplanned | Defective Equipment | FP 390026 - Report of low wire across road - opened Sw 5236 for safety. Broken guy & low LV RR170
|  | F-8698-A | Bickerstaff |  | Maungaturoto CB2 | 2025-02-02 22:01 | 45690.9174 | 2025-02-02 22:53 | 45690.9537 | 0.24451 | 0.012069 | 778 | 15762 | Unplanned | Wildlife | FP 390034 - FENZ 4140475 report of bird strike & fire. Found deceased goose. No line damage found. FENZ clear. Relivened.
|  | F-8701-A | Austin Road |  | Maunu CB1072 | 2025-02-03 05:10 | 45691.2151 | 2025-02-03 06:01 | 45691.2507 | 0.3284 | 0.0063911 | 412 | 21170 | Unplanned | Unknown | FP390035 - Heavy fault - report of bang and flash near Sw 7015. Suspect possum. Checked and relivened
|  | O-5263-B | Tangowahine |  | Dargaville CB8 | 2025-02-03 09:09 | 45691.3812 | 2025-02-03 14:05 | 45691.5868 | 0.050508 | 0.00017064 | 11 | 3256 | Planned | Planned Interruption | Replace poles and conductor
|  | O-5398-B |  |  |  | 2025-02-04 09:04 | 45692.3778 | 2025-02-04 14:46 | 45692.6153 | 0.38198 | 0.0011169 | 72 | 24624 | Planned | Planned Interruption | Replacing Switches 33/1007 & 33/1008 & Recl 1500 Installing New 33kv KL-33/10175 & 33/10176. Remove KL 33/1023
|  | O-5359-B | Thelma Road |  | Mangawhai North CB4 | 2025-02-04 09:23 | 45692.391 | 2025-02-04 14:26 | 45692.6014 | 0.5622 | 0.0019856 | 128 | 36242 | Planned | Planned Interruption | Replace pole 29529, straighten poles 29524 and 29522 and level transformer MC463
|  | O-15952-A |  |  |  | 2025-02-05 09:04 | 45693.3778 | 2025-02-05 13:38 | 45693.5681 | 0.17002 | 0.0006205 | 40 | 10960 | Planned | Planned Interruption | Replace HV poles and cross arms. Refurbish Dsub P176
|  | O-5257-B | Wairere |  | Mareretu CB5 | 2025-02-05 09:46 | 45693.4067 | 2025-02-05 13:03 | 45693.5439 | 0.10424 | 0.00052742 | 34 | 6720 | Planned | Planned Interruption | Replace transformer like for like and replace pole hardware
|  | O-17563-A | Jordan Valley |  | Hikurangi CB1102 | 2025-02-08 20:35 | 45696.8574 | 2025-02-08 23:40 | 45696.9862 | 0.50788 | 0.0073994 | 477 | 32740 | Unplanned | Wildlife | FP390167 Bird strike causing lines down between pole 35013 and pole 324337
|  | F-8725-A | Ararua |  | Mareretu CB2 | 2025-02-10 01:09 | 45698.0476 | 2025-02-10 01:10 | 45698.0485 | 0.013511 | 0.010393 | 670 | 871 | Unplanned | Unknown | T & C
|  | O-5362-B | Onoke |  | Kamo CB8 | 2025-02-10 09:04 | 45698.3779 | 2025-02-10 14:28 | 45698.6024 | 0.4514 | 0.0013961 | 90 | 29099 | Planned | Planned Interruption | Replace links 7267KL with SW 10221
|  | F-8728-A | Mata |  | Ruakaka CB3 | 2025-02-10 10:38 | 45698.4431 | 2025-02-10 11:15 | 45698.4688 | 0.017219 | 0.00046537 | 30 | 1110 | Unplanned | Defective Equipment | FP 390183 - Fit insulator back on to crossarm, upcoming shutdown in area, full replacement will be done then.
|  | O-4726-B |  |  |  | 2025-02-11 09:06 | 45699.3792 | 2025-02-11 13:56 | 45699.5806 | 0.15745 | 0.00054293 | 35 | 10150 | Planned | Planned Interruption | Replace poles 52272(LV) and 10082. Remove poles 10020 and 10025 and associated conductors. Replace crossarm at various poles.
|  | F-8743-A | Norfolk St |  | Alexander St CB1 | 2025-02-11 11:57 | 45699.4979 | 2025-02-11 17:21 | 45699.7229 | 1.1144 | 0.022369 | 1442 | 71841 | Unplanned | Defective Equipment | FP 390230 - HV Cable fault white phase between Pole 307150 & Switch 271. Cable left disconnected and backfed from Whg CB 1092
|  | F-8752-A | Access Rd |  | Ruawai CB1022 | 2025-02-11 23:50 | 45699.9927 | 2025-02-12 00:05 | 45700.0033 | 0.0598 | 0.0052122 | 336 | 3855 | Unplanned | Unknown | 15 min close to Sw 2235
|  | O-5452-B | Mata |  | Ruakaka CB3 | 2025-02-12 09:01 | 45700.3757 | 2025-02-12 14:11 | 45700.591 | 0.33662 | 0.0010859 | 70 | 21700 | Planned | Planned Interruption | HV/LV POLE, ARM & HARDWARE REPLACEMENTS
|  | F-8764-A | Titoki |  | Poroti CB1032 | 2025-02-13 07:58 | 45701.3319 | 2025-02-13 10:03 | 45701.4187 | 0.29667 | 0.0023734 | 153 | 19125 | Unplanned | Human Error | 390275 / Sw 793 Opened without Authorisation, switch had same Chanel and Address as switch 33/1008
|  | F-2537-A | TIK - ONE (Ngunguru) |  | Tikipunga CB92 | 2025-02-13 09:02 | 45701.3766 | 2025-02-13 13:41 | 45701.5702 | 0.31577 | 0.0011324 | 73 | 20356 | Planned | Planned Interruption | Replace various poles from 38178 to EOL
|  | O-5482-B |  |  |  | 2025-02-13 21:36 | 45701.9 | 2025-02-14 06:18 | 45702.2625 | 29.0878 | 0.056698 | 3655 | 1875131 | Planned | Planned Interruption | Replace SW33/1026 with automated switch, Replace links 33/1005 (temp links 17708) with automated switch labelled 33/1005
|  | O-5371-B |  |  |  | 2025-02-14 09:02 | 45702.3764 | 2025-02-14 13:39 | 45702.5686 | 0.15883 | 0.00057396 | 37 | 10239 | Planned | Planned Interruption | HV/LV POLE, ARM, & HARDWARE REPLACEMENTS. UPGRADE Tx U227
|  | F-8803-A | Maungakaramea |  | Maungatapere CB3 | 2025-02-14 17:40 | 45702.7361 | 2025-02-14 19:02 | 45702.7931 | 0.11448 | 0.0013961 | 90 | 7380 | Unplanned | Defective Equipment | 390338 / Isolate area to replace broken crossarm & hardware on pole 12552.
|  | F-8812-A | One Tree Point |  | Ruakaka CB6 | 2025-02-15 05:33 | 45703.2312 | 2025-02-15 07:51 | 45703.3271 | 0.52685 | 0.0065307 | 421 | 33963 | Unplanned | Unknown | FP390347 Tripped O/C A&B phase, patrolled and found no cause, closed in and holding
|  | F-8821-A | One Tree Point |  | Ruakaka CB6 | 2025-02-15 21:28 | 45703.8944 | 2025-02-16 00:01 | 45704.0007 | 0.35191 | 0.019592 | 1263 | 22686 | Unplanned | Unknown | 390352 / Intermittent fault on CB 6 RKA. Patrolled for the second time in 24 hours with no avail. Potential Cracked Insulator.
|  | F-8818-A | Cartwright Rd |  | Onerahi CB6 | 2025-02-15 22:08 | 45703.9225 | 2025-02-16 05:29 | 45704.2285 | 0.44044 | 0.0063601 | 410 | 28393 | Unplanned | Third Party Interference | 390351 / Car Vs Pole 51973. Cut Break and replace pole. BTN
|  | F-8824-A | Montgomery Ave |  | Onerahi CB8 | 2025-02-16 05:13 | 45704.2174 | 2025-02-16 07:10 | 45704.2986 | 0.50972 | 0.032359 | 2086 | 32859 | Unplanned | Vegetation | 390353 / Intermittent tripping. Patrolled and found Bark on lines at pole 36557. Removed & BTN.
|  | O-5506-B | Norfolk St |  | Alexander St CB1 | 2025-02-16 07:32 | 45704.3139 | 2025-02-16 17:24 | 45704.725 | 0.17448 | 0.00029474 | 19 | 11248 | Planned | Planned Interruption | Replace LV Frame with New one. Some LV backfeed done, only 19 ICPs affected
|  | O-5374-B |  |  |  | 2025-02-16 08:44 | 45704.3639 | 2025-02-16 14:10 | 45704.5903 | 0.13654 | 0.00041884 | 27 | 8802 | Planned | Planned Interruption | Replacing poles and cross arms. Late start as agreed with PM
|  | F-8830-A | Mata |  | Ruakaka CB3 | 2025-02-17 08:17 | 45705.3449 | 2025-02-17 12:41 | 45705.5285 | 0.18772 | 0.0016443 | 106 | 12101 | Unplanned | Defective Equipment | FP 390365 - Report of fire on pole, Broken guy wire on 11kV jumper. Pole leaning, isolated for repairs
|  | O-5653-B | Puwera |  | Maungatapere CB7 | 2025-02-17 09:03 | 45705.3771 | 2025-02-17 11:58 | 45705.4986 | 0.38548 | 0.0022028 | 142 | 24850 | Planned | Planned Interruption | Install new HV fuses and tx X524
|  | O-5611-B |  |  |  | 2025-02-17 09:24 | 45705.3917 | 2025-02-17 15:08 | 45705.6306 | 0.17076 | 0.0004964 | 32 | 11008 | Planned | Planned Interruption | HV ARM & HARDWARE REPLACEMENTS
|  | F-8836-A | Dunns Rd |  | Ruawai CB1082 | 2025-02-17 13:31 | 45705.563 | 2025-02-17 13:46 | 45705.5734 | 0.041279 | 0.0027457 | 177 | 2661 | Unplanned | Unknown | 15 min close
|  | O-17641-A | Jordan Valley |  | Hikurangi CB1102 | 2025-02-17 17:14 | 45705.7184 | 2025-02-18 00:31 | 45706.0217 | 0.39018 | 0.0074149 | 478 | 25153 | Unplanned | Third Party Interference | FP390403 Car Vs pole 20319 - 33 & 11kV
|  | O-5377-B | Montgomery Ave |  | Onerahi CB8 | 2025-02-18 09:02 | 45706.3762 | 2025-02-18 14:06 | 45706.5878 | 0.34503 | 0.0011324 | 73 | 22242 | Planned | Planned Interruption | 11kV WIRE AND HARDWARE REPLACEMENTS
|  | O-5644-B | Otonga |  | Hikurangi CB1032 | 2025-02-18 09:19 | 45706.3882 | 2025-02-18 15:08 | 45706.6306 | 0.48735 | 0.0015978 | 103 | 31417 | Planned | Planned Interruption | Replace cable and crucifix at pole 302523
|  | O-5602-B | Hokianga Rd |  | Dargaville CB7 | 2025-02-18 09:33 | 45706.3979 | 2025-02-18 12:29 | 45706.5201 | 0.054604 | 0.00031025 | 20 | 3520 | Planned | Planned Interruption | Level transformer
|  | F-8851-A | Mata |  | Ruakaka CB3 | 2025-02-18 21:42 | 45706.9039 | 2025-02-19 00:20 | 45707.0139 | 0.11037 | 0.0020787 | 134 | 7115 | Unplanned | Defective Equipment | FP390440 FENZ report scrub fire. De-energiised remotely. Broken LV line RO426 caused by preform (fuses in tact). 4 dead cows.
|  | F-8854-A | Swamp North |  | Hikurangi CB1042 | 2025-02-18 22:25 | 45706.934 | 2025-02-19 02:44 | 45707.1142 | 0.62012 | 0.0062825 | 405 | 39976 | Unplanned | Wildlife | FP390441 - 11kV line down & 1 damaged - paradise duck. Additional 104 customers affected for 3h20m due to Sw 674 not operating.
|  | O-5629-B | Taipuha |  | Mareretu CB1 | 2025-02-19 09:02 | 45707.3764 | 2025-02-19 13:17 | 45707.5536 | 0.24148 | 0.00094626 | 61 | 15567 | Planned | Planned Interruption | Replace 11kV arms and pole stays at multiple sites
|  | O-5422-B |  |  |  | 2025-02-19 09:03 | 45707.3771 | 2025-02-19 15:13 | 45707.634 | 1.1364 | 0.0030715 | 198 | 73260 | Planned | Planned Interruption | Remove and decommission pole transformer KT160. Liven new new 100kva ground mount D-sub KT281.
|  | O-5131-B | Ruatangata |  | Kamo CB6 | 2025-02-19 09:06 | 45707.3792 | 2025-02-19 14:50 | 45707.6181 | 0.53363 | 0.0015512 | 100 | 34400 | Planned | Planned Interruption | New TX KR310 installation
|  | O-5365-B | Montgomery Ave |  | Onerahi CB8 | 2025-02-20 09:02 | 45708.3765 | 2025-02-20 11:56 | 45708.4971 | 0.1967 | 0.0011324 | 73 | 12680 | Planned | Planned Interruption | 11kV WIRE AND HARDWARE REPLACEMENTS
|  | O-5647-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-02-20 09:25 | 45708.3924 | 2025-02-20 11:33 | 45708.4812 | 0.081409 | 0.00063601 | 41 | 5248 | Planned | Planned Interruption | Tree clearing work
|  | O-5683-B | Hakaru |  | Kaiwaka CB1032 | 2025-02-20 10:31 | 45708.4382 | 2025-02-20 13:17 | 45708.5535 | 0.046351 | 0.00027922 | 18 | 2988 | Planned | Planned Interruption | Replace HV crossarm at pole 47057 and DOFs MC352
|  | O-5473-B | Puwera |  | Maungatapere CB7 | 2025-02-21 09:09 | 45709.3812 | 2025-02-21 12:57 | 45709.5396 | 0.39966 | 0.0017529 | 113 | 25764 | Planned | Planned Interruption | Crossarm and hardware replacement
|  | O-5488-B | Puwera |  | Maungatapere CB7 | 2025-02-21 09:09 | 45709.3812 | 2025-02-21 12:36 | 45709.525 | 0.057799 | 0.00027922 | 18 | 3726 | Planned | Planned Interruption | Replace crossarms and hardware
|  | O-5851-B | Turiwiri |  | Dargaville CB9 | 2025-02-21 10:06 | 45709.4208 | 2025-02-21 10:20 | 45709.4306 | 0.0008687 | 6.205e-05 | 4 | 56 | Planned | Planned Interruption | Remove reclosing links 3112 & replace with solid links.
|  | O-5575-B | Norfolk St |  | Alexander St CB1 | 2025-02-23 07:14 | 45711.3014 | 2025-02-23 17:24 | 45711.725 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Remove old Transformer WC210 and replace with new Transformer WC210. Liven new Transformer via SW 227 on new siemens switch.
|  | O-5380-B | Taipuha |  | Mareretu CB1 | 2025-02-24 09:03 | 45712.3771 | 2025-02-24 12:28 | 45712.5194 | 0.1431 | 0.00069806 | 45 | 9225 | Planned | Planned Interruption | Replace poles, cross arms, remove 5 span LV and replace LV conductor at 2 sites.
|  | F-151-B | Kaiatea |  | Ngunguru CB1072 | 2025-02-24 16:04 | 45712.6693 | 2025-02-24 17:12 | 45712.7167 | 0.45217 | 0.01061 | 684 | 29149 | Unplanned | Adverse Environment | 390579/ Scrub Fire Kakariki road - Feeder dropped for safety, monitored 11kV & 33kV lines.
|  | F-8890-A | Titoki |  | Poroti CB1032 | 2025-02-25 04:35 | 45713.1908 | 2025-02-25 10:39 | 45713.4437 | 0.62925 | 0.0062825 | 405 | 40564 | Unplanned | Third Party Interference | FP390585 Tripped E/F, 1x HV line down @ pole 50521 (reports of a high load going through this area at time of fault)
|  | F-8893-A | Te Kopuru |  | Dargaville CB2 | 2025-02-25 08:21 | 45713.3479 | 2025-02-25 09:16 | 45713.3864 | 0.41668 | 0.0075235 | 485 | 26861 | Unplanned | Third Party Interference | 390590/ Truck reported hitting LV pole - LVLines down road crossing. Dropped HV Feeder for safety until confirmed safe to liven
|  | O-5530-B | Montgomery Ave |  | Onerahi CB8 | 2025-02-25 09:02 | 45713.3763 | 2025-02-25 12:38 | 45713.5262 | 0.24435 | 0.0011324 | 73 | 15752 | Planned | Planned Interruption | V POLE & HARDWARE REPLACEMENTS. REMOVE HV LINKS 9378 AND HARD TAP SPUR LINE TO OP300 BACK TO MAIN LINE
|  | O-5383-B | Mata |  | Ruakaka CB3 | 2025-02-25 09:06 | 45713.3792 | 2025-02-25 12:33 | 45713.5229 | 0.054588 | 0.00026371 | 17 | 3519 | Planned | Planned Interruption | HV POLE REPLACEMENTS pole 12511 to EOL
|  | O-5572-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-02-25 09:07 | 45713.3799 | 2025-02-25 14:13 | 45713.5924 | 0.16614 | 0.00054293 | 35 | 10710 | Planned | Planned Interruption | replace pole hardware and TX like for like
|  | F-8896-A | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-02-25 14:51 | 45713.619 | 2025-02-25 15:36 | 45713.65 | 0.13299 | 0.0029784 | 192 | 8573 | Unplanned | Third Party Interference | 390614/ Car v Pole causing ABC conductor LV lines down road crossing (near tx O133. Isolated HV for safety.
|  | O-5527-B | Matapouri |  | Ngunguru CB1032 | 2025-02-27 09:01 | 45715.3754 | 2025-02-27 13:03 | 45715.5434 | 0.007508 | 3.1025e-05 | 2 | 484 | Planned | Planned Interruption | Replace HV arm at pole 58907/58908
|  | O-5533-B | Montgomery Ave |  | Onerahi CB8 | 2025-02-27 09:02 | 45715.3767 | 2025-02-27 12:37 | 45715.5255 | 0.24257 | 0.0011324 | 73 | 15637 | Planned | Planned Interruption | HV CONDUCTOR REPLACEMENT
|  | O-5854-B | Pataua |  | Parua Bay CB1 | 2025-02-27 09:08 | 45715.3806 | 2025-02-27 14:02 | 45715.5847 | 0.37853 | 0.0012875 | 83 | 24402 | Planned | Planned Interruption | Pole replacement & Tx upgrade
|  | F-8899-A | Titoki |  | Poroti CB1032 | 2025-02-27 17:39 | 45715.7354 | 2025-02-27 19:57 | 45715.8313 | 0.019266 | 0.00013961 | 9 | 1242 | Unplanned | Vegetation | 390680/Pine trees fallen & leaning over lines. Dropped lines to clear trees & reinstate power
|  | O-5716-B | Coast |  | Dargaville CB6 | 2025-02-28 09:02 | 45716.3764 | 2025-02-28 14:54 | 45716.6208 | 0.27302 | 0.00077562 | 50 | 17600 | Planned | Planned Interruption | Replacing 11kv 400v Poles & Cross arms
|  | F-8905-A | Swamp North |  | Hikurangi CB1042 | 2025-03-01 20:48 | 45717.8667 | 2025-03-02 02:29 | 45718.1035 | 0.41177 | 0.019718 | 1271 | 26542 | Unplanned | Wildlife | 390713 ADMS constantly locking up Two lines down between poles 38815 & 38816 2 x dead ducks
|  | O-5806-B | Mains Ave |  | Tikipunga CB2 | 2025-03-02 09:07 | 45718.3798 | 2025-03-02 10:15 | 45718.4272 | 0.19082 | 0.0027925 | 180 | 12300 | Planned | Planned Interruption | Network Maintenance. Removing KL-7159
|  | O-5731-B | Cairnfield Rd |  | Tikipunga CB5 | 2025-03-02 11:45 | 45718.4893 | 2025-03-02 12:31 | 45718.5214 | 0.1498 | 0.0032424 | 209 | 9656 | Planned | Planned Interruption | Remove KL 7143
|  | O-5803-B | Whau Valley |  | Tikipunga CB1 | 2025-03-02 14:01 | 45718.5839 | 2025-03-02 15:12 | 45718.6333 | 0.26772 | 0.0037698 | 243 | 17257 | Planned | Planned Interruption | Remove links 7130KL from the network
|  | O-5824-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-03-03 09:01 | 45719.3757 | 2025-03-03 11:34 | 45719.4819 | 0.10444 | 0.0006826 | 44 | 6732 | Planned | Planned Interruption | Network Maintenance - rectify high partial discharge at C350
|  | O-5827-B |  |  |  | 2025-03-03 09:14 | 45719.3847 | 2025-03-03 12:16 | 45719.5111 | 0.045176 | 0.00024822 | 16 | 2912 | Planned | Planned Interruption | Rectify partial discharge at SW 4231
|  | F-8914-A | Paparoa |  | Mareretu CB6 | 2025-03-04 01:19 | 45720.0549 | 2025-03-04 04:15 | 45720.1771 | 0.63288 | 0.010999 | 709 | 40795 | Unplanned | Third Party Interference | 390747 / Car Vs Pole 31157 Paparoa. Isolate, Cut Temp break and replace pole.
|  | O-5743-B | Austin Road |  | Maunu CB1072 | 2025-03-05 08:33 | 45721.3562 | 2025-03-05 16:35 | 45721.691 | 0.39147 | 0.00082223 | 53 | 25234 | Planned | Planned Interruption | RMU replacement
|  | O-5635-B |  |  |  | 2025-03-05 09:02 | 45721.3761 | 2025-03-05 14:43 | 45721.6135 | 0.45618 | 0.0013342 | 86 | 29405 | Planned | Planned Interruption | HV crossarm and hardware
|  | F-8929-A | Waipu |  | Ruakaka CB2 | 2025-03-05 15:45 | 45721.6563 | 2025-03-05 16:51 | 45721.7022 | 0.28376 | 0.0042973 | 277 | 18291 | Unplanned | Defective Equipment | 390807 Broken HV insulator at pole 10246
|  | O-5491-B | Swamp North |  | Hikurangi CB1042 | 2025-03-06 09:04 | 45722.3778 | 2025-03-06 14:44 | 45722.6139 | 0.40087 | 0.001179 | 76 | 25840 | Planned | Planned Interruption | Replace 11kV/400v poles, crossarms and hardware Installing Temp Switches 38436 and 38427
|  | F-8947-A | Coast |  | Dargaville CB6 | 2025-03-07 07:39 | 45723.3187 | 2025-03-07 08:17 | 45723.3454 | 0.36153 | 0.016274 | 1049 | 23304 | Unplanned | Wildlife | 390851/ Station Rd Darg.Trip OC Phase ABC. Dead Bird
|  | O-5704-B |  |  |  | 2025-03-07 09:02 | 45723.3762 | 2025-03-07 13:39 | 45723.5688 | 0.56383 | 0.0020323 | 131 | 36344 | Planned | Planned Interruption | Network Maintenance - HV/LV POLE, ARM & HARDWARE REPLACEMENTS
|  | O-5911-B | Ararua |  | Mareretu CB2 | 2025-03-07 09:09 | 45723.3812 | 2025-03-07 14:41 | 45723.6118 | 0.12876 | 0.00038784 | 25 | 8300 | Planned | Planned Interruption | Replace pole, HV & LV crossarms
|  | F-8944-A | Kiripaka Rd |  | Tikipunga CB8 | 2025-03-07 11:52 | 45723.4946 | 2025-03-07 12:37 | 45723.5258 | 0.00069812 | 1.5514e-05 | 1 | 45 | Unplanned | Defective Equipment | 390862 To isolate last fuse to CP 17 - Dion to arrange removeal of CBP 17
|  | F-8962-A | Access Rd |  | Ruawai CB1022 | 2025-03-08 17:05 | 45724.7118 | 2025-03-08 17:20 | 45724.7225 | 0.034611 | 0.0052126 | 336 | 2231 | Unplanned | Unknown | 1 Min Close up to Sw 2235 due to FPIs. 15 Min close on Sw 2235 & BTN
|  | F-8965-A | King Road |  | Mangawhai North CB2 | 2025-03-08 18:55 | 45724.7882 | 2025-03-08 19:44 | 45724.822 | 0.17597 | 0.0036147 | 233 | 11343 | Unplanned | Defective Equipment | 390886 Jumper off the top of the HV fuses MC327
|  | F-8971-A | North Kaiwaka |  | Kaiwaka CB1022 | 2025-03-09 01:37 | 45725.0674 | 2025-03-09 01:52 | 45725.0781 | 0.052436 | 0.0033975 | 219 | 3380 | Unplanned | Unknown | A & B phase OC- unknown
|  | O-5809-B | Tikipunga Hill |  | Tikipunga CB4 | 2025-03-09 09:03 | 45725.3768 | 2025-03-09 09:34 | 45725.3988 | 0.24296 | 0.0076483 | 493 | 15661 | Planned | Planned Interruption | Remove links 6968 from the network
|  | O-5800-B | Charles St |  | Kamo CB2 | 2025-03-09 11:31 | 45725.4798 | 2025-03-09 12:44 | 45725.5308 | 0.17202 | 0.0023426 | 151 | 11088 | Planned | Planned Interruption | Removing KL7429.
|  | O-5869-B | Ararua |  | Mareretu CB2 | 2025-03-11 09:07 | 45727.3801 | 2025-03-11 14:51 | 45727.6186 | 0.90838 | 0.0026528 | 171 | 58553 | Planned | Planned Interruption | Tree clearing work on double circuit
|  | O-5494-B | Swamp North |  | Hikurangi CB1042 | 2025-03-11 09:11 | 45727.3826 | 2025-03-11 14:13 | 45727.5924 | 0.042166 | 0.00013962 | 9 | 2718 | Planned | Planned Interruption | Replacing 11kv 400v poles cross arms & conductor.
|  | O-5746-B | Town Dargaville |  | Dargaville CB3 | 2025-03-11 09:23 | 45727.391 | 2025-03-11 11:36 | 45727.4833 | 0.19602 | 0.0014738 | 95 | 12635 | Planned | Planned Interruption | Repair oil leak in tap changer
|  | O-5947-B | Ararua |  | Mareretu CB2 | 2025-03-11 09:26 | 45727.3931 | 2025-03-11 14:23 | 45727.5993 | 0.15205 | 0.00051195 | 33 | 9801 | Planned | Planned Interruption | replace pole and pole hardware. Replace TX E407 like for like
|  | O-5749-B | Town Dargaville |  | Dargaville CB3 | 2025-03-11 13:12 | 45727.55 | 2025-03-11 15:42 | 45727.6542 | 0.0023271 | 1.5514e-05 | 1 | 150 | Planned | Planned Interruption | Repair oil leak
|  | F-8980-A | Waipu |  | Ruakaka CB2 | 2025-03-11 20:34 | 45727.8573 | 2025-03-11 20:36 | 45727.8581 | 0.016941 | 0.015405 | 993 | 1092 | Unplanned | Wildlife | 390971 / Possum on Tx RR180 Causing Damage to DDOs & LA's
|  | F-154-B | Waipu |  | Ruakaka CB2 | 2025-03-11 20:43 | 45727.8631 | 2025-03-12 00:40 | 45728.0278 | 0.042771 | 0.00055849 | 36 | 2757 | Unplanned | Wildlife | 390971 / Shutdown to repair DDO jumpers & LA's at Tx RR180 that caused feeder fault due to Possum Ref: F-8980-A
|  | O-5932-B | Ararua |  | Mareretu CB2 | 2025-03-12 09:11 | 45728.3826 | 2025-03-12 14:39 | 45728.6104 | 0.040708 | 0.00012411 | 8 | 2624 | Planned | Planned Interruption | Replace pole, TX, HV & LV crossarms
|  | O-5632-B | ToeToe Rd |  | Kioreroa CB7 | 2025-03-12 09:29 | 45728.3951 | 2025-03-12 12:08 | 45728.5056 | 0.222 | 0.0013962 | 90 | 14310 | Planned | Planned Interruption | Network Maintenance replace HV arms and replace TX as per network maintenance pack
|  | F-8986-A | Access Rd |  | Ruawai CB1022 | 2025-03-13 06:23 | 45729.2658 | 2025-03-13 06:24 | 45729.2665 | 0.005647 | 0.0052126 | 336 | 364 | Unplanned | Unknown | O/C A&B phase, closed in 1min F5, unknown (FPI did not activate at Sw 2235)
|  | O-5497-B | Swamp North |  | Hikurangi CB1042 | 2025-03-13 09:01 | 45729.3757 | 2025-03-13 13:45 | 45729.5729 | 0.17183 | 0.00060504 | 39 | 11076 | Planned | Planned Interruption | Replacing 11kv 400v Poles & Cross arms.
|  | F-8992-A | Wharekohe |  | Poroti CB1062 | 2025-03-14 01:22 | 45730.0569 | 2025-03-14 01:23 | 45730.0577 | 0.001179 | 0.001148 | 74 | 76 | Unplanned | Unknown | Tripped O/C AB&C phase, closed in 1min F5, Unknown
|  | O-5953-B | Tangaihi |  | Ruawai CB1032 | 2025-03-14 09:05 | 45730.3785 | 2025-03-14 13:26 | 45730.5597 | 0.38871 | 0.0014893 | 96 | 25056 | Planned | Planned Interruption | Network Maintenance replacing multiple cross arms
|  | O-5872-B | North River |  | Ruakaka CB7 | 2025-03-14 09:09 | 45730.3812 | 2025-03-14 12:09 | 45730.5062 | 0.027925 | 0.00015514 | 10 | 1800 | Planned | Planned Interruption | TX RB192 & fuses RB335 upgrade
|  | F-8995-A | Tamaterau |  | Onerahi CB7 | 2025-03-14 10:39 | 45730.4437 | 2025-03-14 12:52 | 45730.5361 | 0.00619 | 4.6541e-05 | 3 | 399 | Unplanned | Defective Equipment | FP 391024 - Replace crossarm and insulators @ Pole 51816
|  | F-9001-A | Whau Valley |  | Tikipunga CB1 | 2025-03-14 20:02 | 45730.8347 | 2025-03-15 02:59 | 45731.1243 | 0.87865 | 0.0055384 | 357 | 56637 | Unplanned | Third Party Interference | Truck & trailer damaged pole. Temp Break installed to replace.
|  | F-9004-A | Mata |  | Ruakaka CB3 | 2025-03-15 00:05 | 45731.0032 | 2025-03-15 00:29 | 45731.0202 | 0.11609 | 0.0069657 | 449 | 7483 | Unplanned | Unknown | B ph fault - relivened
|  | O-5752-B | Awakino Point |  | Dargaville CB4 | 2025-03-16 09:50 | 45732.4097 | 2025-03-16 10:59 | 45732.4576 | 0.012845 | 0.00018616 | 12 | 828 | Planned | Planned Interruption | Level TX DA53.
|  | O-5503-B | Swamp North |  | Hikurangi CB1042 | 2025-03-18 09:02 | 45734.3764 | 2025-03-18 14:14 | 45734.5931 | 0.049566 | 0.00018616 | 12 | 3195 | Planned | Planned Interruption | Replacing 11v 400v Cross arms & Conductor.
|  | O-5938-B | Ruawai Town |  | Ruawai CB1072 | 2025-03-18 09:08 | 45734.3806 | 2025-03-18 14:45 | 45734.6146 | 0.12548 | 0.00037233 | 24 | 8088 | Planned | Planned Interruption | Install new TX F230 and hardware
|  | F-9022-A | Whatatiri |  | Maungatapere CB8 | 2025-03-19 07:00 | 45735.2916 | 2025-03-19 10:40 | 45735.4444 | 0.16814 | 0.0030252 | 195 | 10838 | Unplanned | Wildlife | FP 391145 - 1x HV line down due to bird strike
|  | O-5500-B | Swamp North |  | Hikurangi CB1042 | 2025-03-19 09:08 | 45735.3806 | 2025-03-19 14:28 | 45735.6028 | 0.19361 | 0.00060504 | 39 | 12480 | Planned | Planned Interruption | Replacing 11kv Conductor.
|  | O-5875-B | Tangowahine |  | Dargaville CB8 | 2025-03-20 09:06 | 45736.3792 | 2025-03-20 12:54 | 45736.5375 | 0.12734 | 0.00055849 | 36 | 8208 | Planned | Planned Interruption | Replace HV and LV crossarms
|  | O-5944-B | Jordan Valley |  | Hikurangi CB1102 | 2025-03-20 09:13 | 45736.3844 | 2025-03-20 15:06 | 45736.6289 | 0.027304 | 7.7569e-05 | 5 | 1760 | Planned | Planned Interruption | Replace HV conductor and hardware
|  | O-5956-B | Hokianga Rd |  | Dargaville CB7 | 2025-03-20 10:40 | 45736.4444 | 2025-03-20 13:41 | 45736.5701 | 0.14602 | 0.00080671 | 52 | 9412 | Planned | Planned Interruption | Transformer maintenance
|  | O-15925-A | Parua Bay |  | Parua Bay CB2 | 2025-03-21 09:07 | 45737.3799 | 2025-03-21 12:54 | 45737.5375 | 0.23595 | 0.0010394 | 67 | 15209 | Planned | Planned Interruption | Tx upgrades
|  | O-6016-B | Coast |  | Dargaville CB6 | 2025-03-21 10:02 | 45737.4181 | 2025-03-21 15:17 | 45737.6368 | 0.2981 | 0.00094634 | 61 | 19215 | Planned | Planned Interruption | Clear trees around 11kv lines
|  | F-9028-A | Titoki |  | Poroti CB1032 | 2025-03-21 10:57 | 45737.4563 | 2025-03-21 11:13 | 45737.4672 | 0.041344 | 0.0047317 | 305 | 2665 | Unplanned | Unknown | Sw 8191 B&C phase indication. Relivened Recl 1520, closed Sw 8191 after 15 mins
|  | F-9031-A | Matapouri |  | Ngunguru CB1032 | 2025-03-21 17:47 | 45737.741 | 2025-03-21 18:54 | 45737.7875 | 0.0062365 | 9.3082e-05 | 6 | 402 | Unplanned | Unknown | FP 391235 - Unknown cause, had to get 2nd man to deliver fuses.
|  | F-9037-A | Titoki |  | Poroti CB1032 | 2025-03-22 17:10 | 45738.7153 | 2025-03-22 17:11 | 45738.716 | 0.01238 | 0.011977 | 772 | 798 | Unplanned | Unknown | E/F No FPI's activated
|  | O-5893-B | Te Kopuru |  | Dargaville CB2 | 2025-03-23 09:01 | 45739.3759 | 2025-03-23 10:58 | 45739.4572 | 0.12709 | 0.001086 | 70 | 8192 | Planned | Planned Interruption | Remove 3134KL from network
|  | O-5587-B | Tangowahine |  | Dargaville CB8 | 2025-03-24 09:06 | 45740.3792 | 2025-03-24 15:57 | 45740.6646 | 0.063761 | 0.00015514 | 10 | 4110 | Planned | Planned Interruption | Replace crossarms. Went over time by 57 mins due to work load.
|  | O-5590-B | Titoki |  | Poroti CB1032 | 2025-03-25 09:03 | 45741.3771 | 2025-03-25 15:03 | 45741.6271 | 0.055849 | 0.00015514 | 10 | 3600 | Planned | Planned Interruption | Replace crossarms and poles
|  | O-6100-B | Hakaru |  | Kaiwaka CB1032 | 2025-03-25 09:23 | 45741.3907 | 2025-03-25 15:33 | 45741.6481 | 0.27599 | 0.00074466 | 48 | 17790 | Planned | Planned Interruption | Network Maintenance - Replace poles & various 11kV works
|  | O-5596-B | Titoki |  | Poroti CB1032 | 2025-03-26 09:05 | 45742.3785 | 2025-03-26 13:55 | 45742.5799 | 0.15297 | 0.00052747 | 34 | 9860 | Planned | Planned Interruption | Pole and crossarm replacement
|  | F-9046-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-03-26 21:16 | 45742.8858 | 2025-03-26 21:36 | 45742.9 | 0.14795 | 0.0072294 | 466 | 9537 | Unplanned | Unknown | Trip A Phase. attempted 15 minute close but timed out causing slight delay to re closing. Closed & BTN.
|  | F-9052-A | Coast |  | Dargaville CB6 | 2025-03-27 07:58 | 45743.3319 | 2025-03-27 11:18 | 45743.4706 | 0.14645 | 0.0013497 | 87 | 9440 | Unplanned | Defective Equipment | FP391328 Replace faulty HV DDO's at Tx L159, damage from burning HV barrel
|  | O-6163-B | Maunu |  | Maunu CB1032 | 2025-03-27 09:02 | 45743.3764 | 2025-03-27 14:43 | 45743.6132 | 0.59231 | 0.0017841 | 115 | 38180 | Planned | Planned Interruption | Connect new cable up pole onto new fuses 10016 to live new TX S140
|  | O-5593-B | Whakapara |  | Hikurangi CB1112 | 2025-03-27 09:03 | 45743.3771 | 2025-03-27 13:09 | 45743.5479 | 0.12594 | 0.00051195 | 33 | 8118 | Planned | Planned Interruption | Replace HV crossarms
|  | O-6115-B | Taipuha |  | Mareretu CB1 | 2025-03-27 09:31 | 45743.3965 | 2025-03-27 13:26 | 45743.5597 | 0.047394 | 0.00020168 | 13 | 3055 | Planned | Planned Interruption | At Pole 33636, connect new DOFs & liven new 50kVA Dsub B265
|  | O-6043-B | Kaka St |  | Whangarei South CB1032 | 2025-03-27 23:19 | 45743.9715 | 2025-03-28 03:41 | 45744.1535 | 0.024388 | 9.3082e-05 | 6 | 1572 | Planned | Planned Interruption | Repair oil leak
|  | F-9055-A | Access Rd |  | Ruawai CB1022 | 2025-03-28 08:08 | 45744.3388 | 2025-03-28 08:24 | 45744.35 | 0.024062 | 0.0051971 | 335 | 1551 | Unplanned | Unknown | Trip OC Phase AC. FPI's Sw 2156 Phase AC. Unknown
|  | O-6199-B | Bickerstaff |  | Maungaturoto CB2 | 2025-03-28 09:09 | 45744.3812 | 2025-03-28 12:35 | 45744.5243 | 0.067112 | 0.00032579 | 21 | 4326 | Planned | Planned Interruption | Install TX D451
|  | O-6304-B | Tangaihi |  | Ruawai CB1032 | 2025-03-28 09:10 | 45744.3819 | 2025-03-28 13:35 | 45744.566 | 0.0082223 | 3.1027e-05 | 2 | 530 | Planned | Planned Interruption | Network Maintenance replace poles and cross arms
|  | F-9058-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-03-28 10:22 | 45744.4321 | 2025-03-28 11:27 | 45744.4773 | 0.10009 | 0.0015359 | 99 | 6452 | Unplanned | Defective Equipment | FP391357 Blown jumper at pole 33872
|  | O-6442-B | Fert. Works |  | Kioreroa CB6 | 2025-03-30 08:08 | 45746.3389 | 2025-03-30 12:01 | 45746.5007 | 0.0072294 | 3.1027e-05 | 2 | 466 | Planned | Planned Interruption | Repair oil leaks
|  | F-9073-A | Otonga |  | Hikurangi CB1032 | 2025-03-31 10:28 | 45747.4361 | 2025-03-31 11:32 | 45747.4806 | 0.26113 | 0.0040801 | 263 | 16832 | Unplanned | Vegetation | FP391402 Trees in line
|  | F-9085-A | Tangaihi |  | Ruawai CB1032 | 2025-03-31 14:13 | 45747.5924 | 2025-03-31 15:01 | 45747.6257 | 0.002234 | 4.6541e-05 | 3 | 144 | Unplanned | Defective Equipment | FP 391423 - Guy wire broken, sitting near HV bushing @ tx K267. 1x HV Fuse blown @ 3311.
¹ Extend table as necessary to disclose information for all individual interruptions
26
27