## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Northpower
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 19 February 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Northpower
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | O-6094-B | Hakaru |  | Kaiwaka CB1032 | 2025-04-02 09:21 | 45749.3896 | 2025-04-02 14:01 | 45749.584 | 0.39537 | 0.001412 | 92 | 25760 | Planned | Planned Interruption | Various pole replacements
10 |  | O-6172-B | Bickerstaff |  | Maungaturoto CB2 | 2025-04-03 09:19 | 45750.3882 | 2025-04-03 16:07 | 45750.6715 | 0.10019 | 0.00024557 | 16 | 6528 | Planned | Planned Interruption | Replace pole 26345 with B11 type, refit HV riser cable 4200, fit new DOFs D450.
11 |  | O-6220-B | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2025-04-03 09:40 | 45750.4028 | 2025-04-03 12:51 | 45750.5354 | 0.0029315 | 1.5348e-05 | 1 | 191 | Planned | Planned Interruption | Cut temporary break at pole 23198
12 |  | F-9142-A | Matapouri |  | Ngunguru CB1032 | 2025-04-03 23:12 | 45750.9667 | 2025-04-04 02:13 | 45751.0924 | 0.5306 | 0.0029315 | 191 | 34571 | Unplanned | Defective Equipment | 391513 / Went to part power and found DDO damaged requiring HV Shutdown.
|  | F-9145-A | Pataua |  | Parua Bay CB1 | 2025-04-03 23:53 | 45750.9952 | 2025-04-04 00:08 | 45751.0059 | 0.042315 | 0.0055407 | 361 | 2757 | Unplanned | Unknown | Trip A Phase. 15 min close & BTN
|  | F-9148-A | Bickerstaff |  | Maungaturoto CB2 | 2025-04-04 00:12 | 45751.0086 | 2025-04-04 08:48 | 45751.3667 | 1.3421 | 0.017113 | 1115 | 87442 | Unplanned | Vegetation | FP391514 Tree through lines @ pole 16226
|  | O-18052-A | Otonga |  | Hikurangi CB1032 | 2025-04-04 03:19 | 45751.1383 | 2025-04-04 13:04 | 45751.5444 | 0.77435 | 0.019784 | 1289 | 50452 | Unplanned | Vegetation | FP 391515 - Repair lines down
|  | F-9157-A | Hakaru |  | Kaiwaka CB1032 | 2025-04-04 16:59 | 45751.7076 | 2025-04-04 19:49 | 45751.8257 | 0.0078276 | 4.6045e-05 | 3 | 510 | Unplanned | Vegetation | 391549 / Isolate HV to remove trees from lines at pole 406691
|  | F-9178-A | Town Dargaville |  | Dargaville CB3 | 2025-04-05 22:44 | 45752.9472 | 2025-04-06 00:46 | 45753.0319 | 0.028087 | 0.00023022 | 15 | 1830 | Unplanned | Third Party Interference | Assess damage after vehicle hit TX DA26
|  | O-6253-B | Maunu Road |  | Whangarei South CB1102 | 2025-04-06 09:13 | 45753.384 | 2025-04-06 11:57 | 45753.4979 | 0.0050342 | 3.0697e-05 | 2 | 328 | Planned | Planned Interruption | Level ground mount D-sub WO214.
|  | F-9184-A | Access Rd |  | Ruawai CB1022 | 2025-04-06 15:59 | 45753.666 | 2025-04-06 16:04 | 45753.6694 | 0.00030697 | 6.1393e-05 | 4 | 20 | Unplanned | Unknown | FP 391578 - Opened HV fuses to inspect. Found 1 fuse operated but didnt drop down
|  | F-9187-A | Awakino Point |  | Dargaville CB4 | 2025-04-07 08:05 | 45754.3368 | 2025-04-07 12:48 | 45754.5333 | 0.29971 | 0.0057556 | 375 | 19527 | Unplanned | Third Party Interference | 391583/ Trip OC Phase BC. Truck V Pole/ Lines Down
|  | O-6175-B | Bickerstaff |  | Maungaturoto CB2 | 2025-04-07 09:09 | 45754.3812 | 2025-04-07 13:54 | 45754.5792 | 0.069988 | 0.00024557 | 16 | 4560 | Planned | Planned Interruption | Connect new HV riser cable to DOFs & Liven Dsub D450.
|  | O-6217-B | Titoki |  | Poroti CB1032 | 2025-04-07 09:15 | 45754.3856 | 2025-04-07 13:47 | 45754.5741 | 0.14995 | 0.00055254 | 36 | 9770 | Planned | Planned Interruption | Replace 11kv poles and cross arms from 50059 to 50730
|  | F-9193-A | Wairere |  | Mareretu CB5 | 2025-04-07 12:30 | 45754.5208 | 2025-04-07 12:47 | 45754.5326 | 0.071461 | 0.0064156 | 418 | 4656 | Unplanned | Defective Equipment | T & C > 15min. Earth fault FPI @ SW 381 due to fauty Tx on F-9193-A
|  | F-9196-A | One Tree Point |  | Ruakaka CB6 | 2025-04-08 10:46 | 45755.4486 | 2025-04-08 13:35 | 45755.566 | 0.53091 | 0.012923 | 842 | 34591 | Unplanned | Defective Equipment | FP 391624 - CB tripped B,C phase. Sectionalised, patrolled lines beyond SW 509. Fault found later on F-9202-A. Broken Stay wire
|  | O-16219-A | Matapouri |  | Ngunguru CB1032 | 2025-04-09 08:32 | 45756.3552 | 2025-04-09 16:48 | 45756.7002 | 0.015241 | 3.0697e-05 | 2 | 993 | Planned | Planned Interruption | Replace poles 58905 and 58906
|  | O-6307-B | Langs Beach |  | Mangawhai North CB3 | 2025-04-09 09:04 | 45756.3778 | 2025-04-09 13:54 | 45756.5792 | 0.022255 | 7.6741e-05 | 5 | 1450 | Planned | Planned Interruption | Replace TX RR205 like for like
|  | O-6229-B | Titoki |  | Poroti CB1032 | 2025-04-09 09:33 | 45756.3979 | 2025-04-09 11:27 | 45756.4771 | 0.069988 | 0.00061393 | 40 | 4560 | Planned | Planned Interruption | Replace pole 50472
|  | O-6268-B | Thelma Road |  | Mangawhai North CB4 | 2025-04-09 09:37 | 45756.4007 | 2025-04-09 15:16 | 45756.6361 | 0.031218 | 9.209e-05 | 6 | 2034 | Planned | Planned Interruption | TX MC 574 Upgrade to 500kVA
|  | O-18112-A | 2nd Ave |  | Alexander St CB3 | 2025-04-10 08:56 | 45757.3722 | 2025-04-10 14:49 | 45757.6174 | 0.010836 | 3.0697e-05 | 2 | 706 | Planned | Planned Interruption | Urgent Repairs - cable needs to be relocated to allow stormwater drainage to be installed.
|  | F-9202-A | One Tree Point |  | Ruakaka CB6 | 2025-04-10 11:16 | 45757.4695 | 2025-04-10 16:40 | 45757.6944 | 0.064232 | 0.008196 | 534 | 4185 | Unplanned | Defective Equipment | 391679 / Tripping from probable line clashing at pole 328382 due to broken stay causing low sag. De Energise & repair stay.
|  | O-6604-B | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2025-04-10 12:44 | 45757.5306 | 2025-04-10 15:30 | 45757.6458 | 0.0025478 | 1.5348e-05 | 1 | 166 | Planned | Planned Interruption | Isolate 11kV for safety for 33kV works
|  | O-6181-B | Turiwiri |  | Dargaville CB9 | 2025-04-11 09:10 | 45758.3819 | 2025-04-11 13:22 | 45758.5569 | 0.17792 | 0.00070602 | 46 | 11592 | Planned | Planned Interruption | replace pole 22368 & replant pole 326500
|  | O-6406-B | Thelma Road |  | Mangawhai North CB4 | 2025-04-11 09:36 | 45758.4 | 2025-04-11 13:03 | 45758.5437 | 0.047656 | 0.00023022 | 15 | 3105 | Planned | Planned Interruption | replace TX MC288 like for like
|  | O-6091-B | Treatment |  | Kioreroa CB2 | 2025-04-13 08:54 | 45760.3708 | 2025-04-13 11:49 | 45760.4924 | 0.037603 | 0.00021488 | 14 | 2450 | Planned | Planned Interruption | Repair oil leak
|  | O-6559-B | Marsden South |  | Bream Bay CB1111 | 2025-04-13 09:02 | 45760.3764 | 2025-04-13 13:47 | 45760.5743 | 0.0043743 | 1.5348e-05 | 1 | 285 | Planned | Planned Interruption | Replace HV arm and DOF's
|  | O-6367-B | Marsden South |  | Bream Bay CB1111 | 2025-04-13 09:11 | 45760.3826 | 2025-04-13 12:12 | 45760.5083 | 0.002778 | 1.5348e-05 | 1 | 181 | Planned | Planned Interruption | Transformer replacement
|  | O-6352-B | Marua |  | Hikurangi CB1022 | 2025-04-14 09:04 | 45761.3778 | 2025-04-14 15:05 | 45761.6285 | 0.47096 | 0.0013046 | 85 | 30685 | Planned | Planned Interruption | Replace poles and crossarms
|  | O-6196-B | Bickerstaff |  | Maungaturoto CB2 | 2025-04-14 09:06 | 45761.3792 | 2025-04-14 11:13 | 45761.4674 | 0.038985 | 0.00030697 | 20 | 2540 | Planned | Planned Interruption | Disestablish Dsub D128, remove Pole 334689 & 1 span of 11kV OH conductors.
|  | O-6118-B | King Road |  | Mangawhai North CB2 | 2025-04-14 09:07 | 45761.3799 | 2025-04-14 11:01 | 45761.459 | 0.0017497 | 1.5348e-05 | 1 | 114 | Planned | Planned Interruption | level transformer
|  | F-9235-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-04-15 05:23 | 45762.2241 | 2025-04-15 05:37 | 45762.234 | 0.058461 | 0.0078276 | 510 | 3809 | Unplanned | Wildlife | Caller reported duck hit power lines at 594 Settlement Rd Lines still in air
|  | O-6007-B | Whatatiri |  | Maungatapere CB8 | 2025-04-15 09:01 | 45762.3756 | 2025-04-15 14:47 | 45762.6158 | 0.49385 | 0.0014274 | 93 | 32176 | Planned | Planned Interruption | Tree Clearing Work
|  | O-6397-B | Tangowahine |  | Dargaville CB8 | 2025-04-15 09:34 | 45762.3986 | 2025-04-15 15:33 | 45762.6479 | 0.72732 | 0.002026 | 132 | 47388 | Planned | Planned Interruption | Pole Replacement to allow for the safe transport of high loads
|  | F-9259-A | Swamp North |  | Hikurangi CB1042 | 2025-04-16 02:29 | 45763.1036 | 2025-04-16 02:44 | 45763.114 | 0.042607 | 0.0062007 | 404 | 2776 | Unplanned | Adverse Weather | Unknown - Trip OC ABC. FPIs activated Sw 672 Phase ABC
|  | F-9268-A | Langs Beach |  | Mangawhai North CB3 | 2025-04-16 04:14 | 45763.1764 | 2025-04-16 08:25 | 45763.3506 | 3.1114 | 0.047027 | 3064 | 202723 | Unplanned | Human Error | Protection settings incorrect at substation. Settings changes made. No fault found.
|  | F-9271-A | Brynderwyn |  | Maungaturoto CB1 | 2025-04-16 05:26 | 45763.2261 | 2025-04-16 05:53 | 45763.2453 | 0.079074 | 0.0028548 | 186 | 5152 | Unplanned | Adverse Weather | Trip EF - Unknown
|  | F-9274-A | Wairere |  | Mareretu CB5 | 2025-04-16 06:26 | 45763.2679 | 2025-04-16 06:41 | 45763.2783 | 0.096587 | 0.0064463 | 420 | 6293 | Unplanned | Adverse Weather | B phase OC - close >15min
|  | F-9280-A | Maungakaramea |  | Maungatapere CB3 | 2025-04-16 08:39 | 45763.3604 | 2025-04-16 12:41 | 45763.5285 | 0.30979 | 0.002026 | 132 | 20184 | Unplanned | Vegetation | FP 391823 - Removed tree from OH line
|  | F-9283-A | Waipu |  | Ruakaka CB2 | 2025-04-16 08:54 | 45763.3708 | 2025-04-16 12:24 | 45763.5167 | 0.28394 | 0.015241 | 993 | 18500 | Unplanned | Defective Equipment | FP 391826 - Repaired lines down
|  | F-9286-A | Rewa Rewa RD |  | Whangarei South CB1082 | 2025-04-16 09:55 | 45763.4132 | 2025-04-16 10:14 | 45763.4264 | 0.27189 | 0.014335 | 934 | 17715 | Unplanned | Adverse Weather | A B phase OC - close >15min
|  | F-9295-A | Wairere |  | Mareretu CB5 | 2025-04-16 11:07 | 45763.4633 | 2025-04-16 23:35 | 45763.9826 | 2.1247 | 0.025294 | 1648 | 138433 | Unplanned | Defective Equipment | Lines down 391815
|  | F-9298-A | Ruatangata |  | Kamo CB6 | 2025-04-16 11:14 | 45763.4678 | 2025-04-16 14:33 | 45763.6064 | 1.5011 | 0.011496 | 749 | 97804 | Unplanned | Vegetation | FP 391851 - Cleared trees on OH line
|  | F-9301-A | Kaka St |  | Whangarei South CB1032 | 2025-04-16 11:41 | 45763.4868 | 2025-04-16 13:43 | 45763.5715 | 0.43937 | 0.0057249 | 373 | 28627 | Unplanned | Defective Equipment | FP 391852 - Repaired broken dead end
|  | F-9304-A | King Road |  | Mangawhai North CB2 | 2025-04-16 11:53 | 45763.4953 | 2025-04-16 13:54 | 45763.5795 | 0.31892 | 0.0062774 | 409 | 20779 | Unplanned | Adverse Weather | FP 391855 - sectionalised fdr upto SW 327. Lines patrolled, no fault found
|  | F-9307-A | Springs Flat |  | Kamo CB1 | 2025-04-16 16:04 | 45763.6693 | 2025-04-17 03:29 | 45764.1451 | 1.1053 | 0.0081192 | 529 | 72017 | Unplanned | Vegetation | FP 391888 - Clear Trees
|  | F-9310-A | Beach Road |  | Onerahi CB2 | 2025-04-16 16:18 | 45763.6792 | 2025-04-16 17:09 | 45763.7146 | 0.037573 | 0.00073672 | 48 | 2448 | Unplanned | Defective Equipment | FP391877 Jumper off bottom of HV fuses
|  | F-9313-A | Bickerstaff |  | Maungaturoto CB2 | 2025-04-16 16:29 | 45763.6871 | 2025-04-16 16:50 | 45763.7016 | 0.21897 | 0.011926 | 777 | 14267 | Unplanned | Adverse Weather | No FPIs. Closed > 15min
|  | F-9319-A | Whatatiri |  | Maungatapere CB8 | 2025-04-16 20:14 | 45763.8429 | 2025-04-21 12:35 | 45768.5243 | 9.223 | 0.023606 | 1639 | 601009 | Unplanned | Vegetation | FP 391910, 391992, 392334, 3922210 Multiple work sites on same feeder over multiple days.
|  | F-9328-A | Ruatangata |  | Kamo CB6 | 2025-04-16 21:43 | 45763.9045 | 2025-04-18 13:10 | 45765.5486 | 9.1366 | 0.013629 | 888 | 595286 | Unplanned | Defective Equipment | 391918 Lines down near pole 54250
|  | F-9331-A | ToeToe Rd |  | Kioreroa CB7 | 2025-04-16 21:57 | 45763.9149 | 2025-04-16 22:51 | 45763.9524 | 0.35342 | 0.0094238 | 614 | 23027 | Unplanned | Adverse Weather | Trip OC AB FPI Sw 10094 Phase AB.
|  | F-9334-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-04-16 21:58 | 45763.9155 | 2025-04-17 16:09 | 45764.6729 | 4.3927 | 0.01409 | 918 | 286200 | Unplanned | Vegetation | lines down - TBV
|  | F-9337-A | Swamp North |  | Hikurangi CB1042 | 2025-04-16 22:57 | 45763.9563 | 2025-04-18 15:27 | 45765.6437 | 11.6916 | 0.010084 | 657 | 761752 | Unplanned | Adverse Weather | 391995 HIK CB 1042 tripped on OC, full line patrol/ liven in stages
|  | F-9340-A | Maungakaramea |  | Maungatapere CB3 | 2025-04-16 23:23 | 45763.9745 | 2025-04-17 17:42 | 45764.7375 | 4.7334 | 0.0092396 | 602 | 308399 | Unplanned | Adverse Weather | Patrolled and livened in sections
|  | F-9343-A | Jordan Valley |  | Hikurangi CB1102 | 2025-04-16 23:27 | 45763.9768 | 2025-04-18 16:48 | 45765.7 | 15.0443 | 0.0073365 | 478 | 980197 | Unplanned | Adverse Weather | Storm. Patrol lines Via Helicopter & re liven accordingly.
|  | F-175-B | Springs Flat |  | Kamo CB1 | 2025-04-17 00:10 | 45764.0072 | 2025-04-17 15:23 | 45764.6411 | 2.831 | 0.0066611 | 434 | 184453 | Unplanned | Adverse Weather | Patrolled no fault found - refer F-175-B Excludes 95 ICPs (Sw 6050 already open F-9307-A)
|  | F-9346-A | Coast |  | Dargaville CB6 | 2025-04-17 00:16 | 45764.011 | 2025-04-17 14:46 | 45764.6153 | 2.2059 | 0.0043436 | 283 | 143724 | Unplanned | Vegetation | Lines down, trees cleared
|  | F-9349-A | Paranui |  | Tikipunga CB6 | 2025-04-17 00:25 | 45764.0176 | 2025-04-17 04:17 | 45764.1785 | 2.347 | 0.011312 | 737 | 152915 | Unplanned | Adverse Weather | Relivened in sections - no cause found. Tripped same time as CB 92 TIK-ONE 33kV
|  | F-9352-A | Matapouri |  | Ngunguru CB1032 | 2025-04-17 00:25 | 45764.0176 | 2025-04-17 05:20 | 45764.2224 | 7.6236 | 0.16447 | 10716 | 496707 | Unplanned | Adverse Weather | Storm. Patrol lines & liven accordingly
|  | F-9355-A | Tangaihi |  | Ruawai CB1032 | 2025-04-17 00:26 | 45764.0181 | 2025-04-18 14:53 | 45765.6203 | 5.0336 | 0.034211 | 2229 | 327956 | Unplanned | Defective Equipment | 392029 Binder Repairs pole 28651
|  | F-40-C | Maungakaramea |  | Maungatapere CB3 | 2025-04-17 00:52 | 45764.0359 | 2025-04-19 09:48 | 45766.4083 | 2.2792 | 0.0092396 | 602 | 148498 | Unplanned | Vegetation | 391926 Lines down pole 307627
|  | F-9358-A | North River |  | Ruakaka CB7 | 2025-04-17 00:55 | 45764.0381 | 2025-04-18 17:50 | 45765.7431 | 6.8886 | 0.0057249 | 373 | 448819 | Unplanned | Defective Equipment | 391936 Broken x-arm pole 308055
|  | F-9361-A | Kiripaka Rd |  | Tikipunga CB8 | 2025-04-17 01:05 | 45764.0455 | 2025-04-18 17:00 | 45765.7083 | 13.2665 | 0.013015 | 848 | 864364 | Unplanned | Vegetation | Storm. Patrol lines and liven accordingly. Found & Repaired lines/trees on lines between pole 40278 & 40279.
|  | F-178-B | Puwera |  | Maungatapere CB7 | 2025-04-17 01:18 | 45764.0539 | 2025-04-19 17:00 | 45766.7083 | 9.6066 | 0.0052491 | 342 | 625909 | Unplanned | Defective Equipment | Repaired spragged lines/ lines down - various locations 391994
|  | F-9367-A | North Dargaville |  | Dargaville CB1 | 2025-04-17 01:59 | 45764.0826 | 2025-04-18 13:25 | 45765.559 | 2.4939 | 0.0023329 | 152 | 162485 | Unplanned | Defective Equipment | Repair lines down between poles 328237 and 348744
|  | F-9370-A | Access Rd |  | Ruawai CB1022 | 2025-04-17 02:19 | 45764.0967 | 2025-04-18 16:45 | 45765.6979 | 2.0694 | 0.010253 | 668 | 134831 | Unplanned | Defective Equipment | HV lines down - between pole 44794 and pole 44795
|  | F-9373-A | Swamp South |  | Hikurangi CB1092 | 2025-04-17 02:59 | 45764.1242 | 2025-04-18 15:49 | 45765.659 | 0.31717 | 0.00035301 | 23 | 20665 | Unplanned | Defective Equipment | Lines down
|  | F-9376-A | Otonga |  | Hikurangi CB1032 | 2025-04-17 03:17 | 45764.1369 | 2025-04-17 14:43 | 45764.6132 | 4.7153 | 0.0091476 | 596 | 307221 | Unplanned | Defective Equipment | Lines down
|  | F-9379-A | North Kaiwaka |  | Kaiwaka CB1022 | 2025-04-17 03:35 | 45764.1492 | 2025-04-17 20:22 | 45764.8486 | 3.1351 | 0.0033459 | 218 | 204263 | Unplanned | Adverse Weather | FP 392028 - Patroled lines, no fault find. Low priority feeder.
|  | F-9382-A | Langs Beach |  | Mangawhai North CB3 | 2025-04-17 03:59 | 45764.1659 | 2025-04-17 09:41 | 45764.4035 | 3.4472 | 0.012939 | 843 | 224597 | Unplanned | Adverse Weather | No fault found
|  | F-187-B | Bickerstaff |  | Maungaturoto CB2 | 2025-04-17 04:05 | 45764.1701 | 2025-04-19 13:50 | 45766.5764 | 5.4879 | 0.026552 | 1730 | 357558 | Unplanned | Vegetation | EF - Trees in lines at various places.
|  | F-9385-A | Golden Bay Nth |  | Maungatapere POS CB1332 | 2025-04-17 04:24 | 45764.183 | 2025-04-17 09:25 | 45764.3924 | 3.9455 | 0.02049 | 1335 | 257062 | Unplanned | Defective Equipment | Conductor off insulator pole 416904
|  | F-9388-A | Maunu Road |  | Whangarei South CB1102 | 2025-04-17 04:24 | 45764.1833 | 2025-04-17 07:58 | 45764.3319 | 1.0612 | 0.014366 | 936 | 69144 | Unplanned | Vegetation | FP 391965 - Cleared Trees
|  | F-9391-A | Paparoa |  | Mareretu CB6 | 2025-04-17 04:31 | 45764.1881 | 2025-04-17 13:51 | 45764.5771 | 4.6106 | 0.0090555 | 590 | 300399 | Unplanned | Adverse Weather | Patrolled feeder and livened in sections - no fault found
|  | F-9394-A | Dunns Rd |  | Ruawai CB1082 | 2025-04-17 04:38 | 45764.1933 | 2025-04-19 13:01 | 45766.5424 | 5.991 | 0.0027166 | 177 | 390337 | Unplanned | Vegetation | Trees in lines
|  | F-9397-A | Mata |  | Ruakaka CB3 | 2025-04-17 04:57 | 45764.2061 | 2025-04-19 12:15 | 45766.5104 | 7.1234 | 0.014228 | 927 | 464119 | Unplanned | Vegetation | 391937 LV lines down
|  | F-9400-A | Commercial |  | Mangawhai Central CB1042 | 2025-04-17 06:37 | 45764.2757 | 2025-04-17 06:56 | 45764.2887 | 0.24305 | 0.013522 | 881 | 15836 | Unplanned | Adverse Weather | Trip A & B & Closed BTN
|  | F-9412-A | Tangowahine |  | Dargaville CB8 | 2025-04-17 09:13 | 45764.3837 | 2025-04-17 17:51 | 45764.7438 | 0.4687 | 0.0088866 | 579 | 30538 | Unplanned | Defective Equipment | Broken crossarm at pole 36606
|  | F-9415-A | Turiwiri |  | Dargaville CB9 | 2025-04-17 09:50 | 45764.41 | 2025-04-18 17:48 | 45765.7417 | 5.7171 | 0.0076895 | 501 | 372492 | Unplanned | Defective Equipment | 392016 Lines down pole 19063
|  | F-202-B | Tamaterau |  | Onerahi CB7 | 2025-04-17 11:00 | 45764.4583 | 2025-04-17 14:34 | 45764.6069 | 1.7277 | 0.0086257 | 562 | 112564 | Unplanned | Adverse Weather | Trip Unknown
|  | F-193-B | Whakapara |  | Hikurangi CB1112 | 2025-04-17 11:18 | 45764.4709 | 2025-04-17 17:32 | 45764.7306 | 4.7641 | 0.01673 | 1090 | 310398 | Unplanned | Defective Equipment | Patrolled. Replaced stay anchor at pole 12425. Livened in sections
|  | F-205-B | Matapouri |  | Ngunguru CB1032 | 2025-04-17 13:36 | 45764.5667 | 2025-04-17 16:54 | 45764.7042 | 0.079013 | 0.00039905 | 26 | 5148 | Unplanned | Vegetation | Lines down pole 309563
|  | F-208-B | Cartwright Rd |  | Onerahi CB6 | 2025-04-17 13:53 | 45764.5784 | 2025-04-17 17:26 | 45764.7266 | 0.88774 | 0.012309 | 802 | 57840 | Unplanned | Vegetation | Lines down from Pole 306274 causing trip.
|  | F-9430-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-04-17 20:08 | 45764.8389 | 2025-04-19 14:17 | 45766.5951 | 0.077631 | 3.0697e-05 | 2 | 5058 | Unplanned | Defective Equipment | 392053 Links removed to repair connections
|  | F-9433-A | Kaka St |  | Whangarei South CB1032 | 2025-04-17 21:24 | 45764.8917 | 2025-04-17 23:29 | 45764.9785 | 0.47893 | 0.0057249 | 373 | 31204 | Unplanned | Vegetation | 392073 Palm frond over the line Cnr Wood & Albert St again
|  | F-9436-A | Parua Bay |  | Parua Bay CB2 | 2025-04-18 02:36 | 45765.1083 | 2025-04-18 04:28 | 45765.1861 | 0.38334 | 0.0034227 | 223 | 24976 | Unplanned | Defective Equipment | 392074 JHV jumper off at pole 25100
|  | F-9439-A | Wharekohe |  | Poroti CB1062 | 2025-04-18 05:44 | 45765.2389 | 2025-04-18 05:45 | 45765.2398 | 0.0014427 | 0.0011358 | 74 | 94 | Unplanned | Adverse Weather | O/C trip
|  | F-217-B | Marua |  | Hikurangi CB1022 | 2025-04-18 13:13 | 45765.5507 | 2025-04-18 20:02 | 45765.8347 | 0.075329 | 0.00018418 | 12 | 4908 | Unplanned | Adverse Weather | 392153 3 x blown 11kV fuses
|  | F-9469-A | Town Dargaville |  | Dargaville CB3 | 2025-04-18 19:48 | 45765.8253 | 2025-04-19 15:01 | 45766.6257 | 0.7775 | 0.01676 | 1092 | 50657 | Unplanned | Lightning | 392157 Blown insulator pole 61585
|  | F-9547-A | Mata |  | Ruakaka CB3 | 2025-04-19 09:14 | 45766.3846 | 2025-04-20 10:52 | 45767.4528 | 0.04408 | 0.00046045 | 30 | 2872 | Unplanned | Defective Equipment | 392203 Damaged 11kV links
|  | F-9502-A | Waipu |  | Ruakaka CB2 | 2025-04-19 09:17 | 45766.3868 | 2025-04-19 10:10 | 45766.4236 | 0.0073211 | 0.00013813 | 9 | 477 | Unplanned | Lightning | 392167 3 x 11kV fuses blown
|  | F-9526-A | Waipu |  | Ruakaka CB2 | 2025-04-19 11:42 | 45766.4875 | 2025-04-19 16:57 | 45766.7063 | 0.019339 | 6.1393e-05 | 4 | 1260 | Unplanned | Adverse Weather | 392199 Blown 16A fuses - Tech to test cable
|  | F-9595-A | Springs Flat |  | Kamo CB1 | 2025-04-21 11:04 | 45768.4609 | 2025-04-21 11:53 | 45768.4949 | 0.415 | 0.015747 | 1026 | 27039 | Unplanned | Wildlife | 392339/ Trip EF. loud bang reported, bird found as cause
|  | O-6454-B | Springs Flat |  | Kamo CB1 | 2025-04-22 09:07 | 45769.3799 | 2025-04-22 12:06 | 45769.5042 | 0.54672 | 0.0030543 | 199 | 35621 | Planned | Planned Interruption | Replace pole and hardware
|  | F-229-B | Parua Bay |  | Parua Bay CB2 | 2025-04-22 16:17 | 45769.6785 | 2025-04-22 16:39 | 45769.6936 | 0.17723 | 0.0090708 | 591 | 11547 | Unplanned | Wildlife | 392419/ Trip OC Phase BC - Starling bird found as cause
|  | O-6457-B | Coast |  | Dargaville CB6 | 2025-04-23 09:08 | 45770.3806 | 2025-04-23 12:14 | 45770.5097 | 0.019983 | 0.00010744 | 7 | 1302 | Planned | Planned Interruption | Installation of new Tx DA141
|  | F-9631-A | Marua |  | Hikurangi CB1022 | 2025-04-24 02:36 | 45771.1082 | 2025-04-24 12:45 | 45771.5312 | 0.34753 | 0.0087332 | 709 | 22771 | Unplanned | Vegetation | 392473/ Lines down & broken pole head
|  | O-6466-B | Jordan Valley |  | Hikurangi CB1102 | 2025-04-24 09:06 | 45771.3792 | 2025-04-24 13:10 | 45771.5486 | 0.082389 | 0.00033766 | 22 | 5368 | Planned | Planned Interruption | Rebuild TX structure
|  | O-6319-B | Te Kopuru |  | Dargaville CB2 | 2025-04-24 09:16 | 45771.3861 | 2025-04-24 11:50 | 45771.4931 | 0.572 | 0.0037143 | 242 | 37268 | Planned | Planned Interruption | Replace pole #14356 with B11 to assist with lv height
|  | F-9640-A | North River |  | Ruakaka CB7 | 2025-04-24 17:46 | 45771.7403 | 2025-04-25 01:02 | 45772.0431 | 1.0004 | 0.01742 | 1135 | 65177 | Unplanned | Defective Equipment | 392518/ HV Line down across water between 418289 & 40891. Could not bfeed more ICP's on initially due to faulty Sw 5455
|  | F-9658-A | Montgomery Ave |  | Onerahi CB8 | 2025-04-27 06:52 | 45774.2863 | 2025-04-27 12:21 | 45774.5146 | 0.74631 | 0.016039 | 1045 | 48625 | Unplanned | Vegetation | FP392535 Trees on lines, lines down btwn poles 36357 & 36356
|  | F-9661-A | Western Hills Dr |  | Alexander St CB7 | 2025-04-27 16:44 | 45774.6972 | 2025-04-27 18:50 | 45774.7847 | 0.12639 | 0.0018111 | 118 | 8235 | Unplanned | Defective Equipment | 392542 / Isolate to replace broken DDOs at Tx WC277.
|  | F-9664-A | Ruatangata |  | Kamo CB6 | 2025-04-27 18:34 | 45774.7736 | 2025-04-27 20:04 | 45774.8361 | 0.004144 | 4.6045e-05 | 3 | 270 | Unplanned | Vegetation | 392546 / Tree Vs Lines causing 3 x HV Fuses to blow on L 7823. Removed Trees & Livened BTN
|  | O-6400-B | Tangaihi |  | Ruawai CB1032 | 2025-04-28 09:36 | 45775.4 | 2025-04-28 12:50 | 45775.5347 | 0.083372 | 0.00042975 | 28 | 5432 | Planned | Planned Interruption | Repair oil leak on HV bushing
|  | O-6571-B | North River |  | Ruakaka CB7 | 2025-04-28 10:05 | 45775.4201 | 2025-04-28 14:17 | 45775.5951 | 0.15084 | 0.00059858 | 39 | 9828 | Planned | Planned Interruption | Connect new 11kV line up to existing network at pole 301091 Liven new TX RB339
|  | O-6436-B | Tangowahine |  | Dargaville CB8 | 2025-04-28 10:13 | 45775.4257 | 2025-04-28 14:24 | 45775.6 | 0.14254 | 0.00056789 | 37 | 9287 | Planned | Planned Interruption | Remove vegetation around 11kv lines from pole #37870 to the end of line
|  | O-6535-B | Town |  | Hikurangi CB1082 | 2025-04-28 13:01 | 45775.5424 | 2025-04-28 14:56 | 45775.6222 | 0.095313 | 0.00082881 | 54 | 6210 | Planned | Planned Interruption | Retention lv and 11kv lines from pole #300353
|  | F-9697-A | Tangaihi |  | Ruawai CB1032 | 2025-04-29 11:18 | 45776.4708 | 2025-04-29 12:49 | 45776.534 | 0.0083801 | 9.209e-05 | 6 | 546 | Unplanned | Defective Equipment | 392616/ Jumper off Load side HV fuses 3290
|  | F-9703-A | Ruatangata |  | Kamo CB6 | 2025-04-29 19:25 | 45776.809 | 2025-04-29 20:29 | 45776.8535 | 0.097247 | 0.0015195 | 99 | 6336 | Unplanned | Third Party Interference | 392639 / Isolate to replace Pole 910556 after car v pole.
|  | O-6298-B | Puwera |  | Maungatapere CB7 | 2025-04-30 09:04 | 45777.3778 | 2025-04-30 15:23 | 45777.641 | 0.21523 | 0.00056789 | 37 | 14023 | Planned | Planned Interruption | HV/LV ARM AND HARDWARE REPLACEMENTS
|  | F-9715-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-04-30 09:11 | 45777.3827 | 2025-04-30 09:54 | 45777.4125 | 0.065261 | 0.0015195 | 99 | 4252 | Unplanned | Third Party Interference | 392656/ Isolated HV for Safety - LV Lines down. Reported metal thrucks through area prior
|  | O-6565-B | Swamp North |  | Hikurangi CB1042 | 2025-04-30 10:00 | 45777.4167 | 2025-04-30 12:27 | 45777.5188 | 0.10604 | 0.00072137 | 47 | 6909 | Planned | Planned Interruption | Replace SW 674 - Delayed on start & restoration,started late & rain through the area for LL works
|  | F-9718-A | North River |  | Ruakaka CB7 | 2025-04-30 19:58 | 45777.8322 | 2025-05-01 05:52 | 45778.2444 | 1.1448 | 0.016991 | 1107 | 74588 | Unplanned | Defective Equipment | FP392676 Tripped E/F, intermittant fault - Found broken LA @ pole 307816
|  | O-6259-B | Marsden South |  | Bream Bay CB1111 | 2025-05-01 09:02 | 45778.3764 | 2025-05-01 14:45 | 45778.6146 | 0.031587 | 9.209e-05 | 6 | 2058 | Planned | Planned Interruption | Install new tx RP 847
|  | O-6550-B | Access Road |  | Ruawai CB1022 | 2025-05-01 09:12 | 45778.3836 | 2025-05-01 14:23 | 45778.5994 | 0.56297 | 0.0018111 | 118 | 36680 | Planned | Planned Interruption | Pole 44530 replacement
|  | O-6430-B | Coast |  | Dargaville CB6 | 2025-05-01 09:56 | 45778.4139 | 2025-05-01 15:41 | 45778.6535 | 0.17474 | 0.00050649 | 33 | 11385 | Planned | Planned Interruption | Pole replacements to increase road crossing height for future Safe Transport of a High Load
|  | F-9721-A | Poroti |  | Maungatapere CB2 | 2025-05-01 11:23 | 45778.4744 | 2025-05-01 12:27 | 45778.5188 | 0.25113 | 0.0095466 | 622 | 16362 | Unplanned | Vegetation | 392707/ Trip AB EF - Cleared branches from Proctor Rd
|  | F-9727-A | Tangaihi |  | Ruawai CB1032 | 2025-05-01 13:04 | 45778.5444 | 2025-05-01 16:08 | 45778.6722 | 0.013813 | 0.00013813 | 9 | 900 | Unplanned | Defective Equipment | 392697 Replaced tail blown off HV fuses and replaced tx
|  | O-6556-B | Tangowahine |  | Dargaville CB8 | 2025-05-02 09:08 | 45779.3806 | 2025-05-02 14:30 | 45779.6042 | 0.32124 | 0.00099764 | 65 | 20930 | Planned | Planned Interruption | Various poles to be replaced
|  | O-6487-B | Te Kopuru |  | Dargaville CB2 | 2025-05-02 09:11 | 45779.3826 | 2025-05-02 12:43 | 45779.5299 | 0.23428 | 0.0011051 | 72 | 15264 | Planned | Planned Interruption | Bind 11kV to pole 309846
|  | O-18130-A | Tutukaka Block |  | Ngunguru CB1082 | 2025-05-02 09:34 | 45779.3986 | 2025-05-02 12:19 | 45779.5132 | 0.0050649 | 3.0697e-05 | 2 | 330 | Planned | Planned Interruption | Level D-Sub NK169
|  | F-9733-A | ONE - KIO |  | Onerahi CB52 | 2025-05-02 20:50 | 45779.8681 | [6 empty] | Unplanned | Unknown | 392726/ Trip EF, 33kV ONE-KIO. No ICP's lost
|  | O-6499-B | Water Treatment |  | Kioreroa CB3 | 2025-05-04 09:02 | 45781.3764 | 2025-05-04 13:22 | 45781.5569 | 0.019953 | 7.6741e-05 | 5 | 1300 | Planned | Planned Interruption | Replace SW 9061 & Pole
|  | O-6547-B | Town Dargaville |  | Dargaville CB3 | 2025-05-05 09:15 | 45782.3854 | 2025-05-05 15:48 | 45782.6583 | 1.4356 | 0.0036529 | 238 | 93534 | Planned | Planned Interruption | Pole 32703-32742 - replace wrap locks with Armour rods
|  | O-6607-B | King Road |  | Mangawhai North CB2 | 2025-05-05 10:17 | 45782.4285 | 2025-05-05 13:25 | 45782.559 | 0.0086564 | 4.6045e-05 | 3 | 564 | Planned | Planned Interruption | Raise TX MC 569
|  | F-9745-A | Tangaihi |  | Ruawai CB1032 | 2025-05-05 15:53 | 45782.6618 | 2025-05-05 15:56 | 45782.6639 | 0.00013813 | 4.6045e-05 | 3 | 9 | Unplanned | Unknown | FP 392806 reload and replace HV fuses
|  | O-6628-B | Kokopu |  | Poroti CB1022 | 2025-05-06 09:02 | 45783.3764 | 2025-05-06 13:55 | 45783.5799 | 0.42722 | 0.0014581 | 95 | 27835 | Planned | Planned Interruption | TRANSFORMER UPGRADE, HV/LV ARM & HARDWARE REPLACEMENTS
|  | O-6187-B | Ararua |  | Mareretu CB2 | 2025-05-06 09:06 | 45783.3792 | 2025-05-06 14:28 | 45783.6028 | 0.014826 | 4.6045e-05 | 3 | 966 | Planned | Planned Interruption | replace poles and TX E247 like for like - TBV
|  | O-6286-B | Springs Flat |  | Kamo CB1 | 2025-05-06 09:10 | 45783.3819 | 2025-05-06 12:48 | 45783.5333 | 0.31786 | 0.0014581 | 95 | 20710 | Planned | Planned Interruption | Refurbish Dsub KS173 and replace and replant poles
|  | O-6613-B | Montgomery Ave |  | Onerahi CB8 | 2025-05-07 09:04 | 45784.3778 | 2025-05-07 15:23 | 45784.641 | 0.55106 | 0.0014734 | 96 | 35904 | Planned | Planned Interruption | Poles and Hardware replacements. Upgrade Transfomer OP280
|  | O-6508-B | Dunns Rd |  | Ruawai CB1082 | 2025-05-08 09:02 | 45785.3764 | 2025-05-08 14:36 | 45785.6083 | 0.13328 | 0.00039905 | 26 | 8684 | Planned | Planned Interruption | Tree Clearing Work
|  | O-6631-B | Pataua |  | Parua Bay CB1 | 2025-05-08 09:04 | 45785.3778 | 2025-05-08 13:25 | 45785.559 | 0.21632 | 0.00082881 | 54 | 14094 | Planned | Planned Interruption | HV CONDUCTOR, ARM & HARDWARE REPLACEMENTS
|  | O-6595-B | North River |  | Ruakaka CB7 | 2025-05-08 09:06 | 45785.3792 | 2025-05-08 13:06 | 45785.5458 | 0.14366 | 0.00059858 | 39 | 9360 | Planned | Planned Interruption | Install new HV poles, lines and TX labelled RB340
|  | O-6184-B | Ararua |  | Mareretu CB2 | 2025-05-08 09:07 | 45785.3799 | 2025-05-08 14:32 | 45785.6056 | 0.089787 | 0.00027627 | 18 | 5850 | Planned | Planned Interruption | Straighten & replace poles and hardware. Replace transformer E282 with a 50kva - same number
|  | O-18190-A | Kokopu |  | Poroti CB1022 | 2025-05-08 09:11 | 45785.3826 | 2025-05-08 11:30 | 45785.4792 | 0.046935 | 0.00033766 | 22 | 3058 | Planned | Planned Interruption | Level D-Sub P451
|  | O-6658-B | Te Hihi |  | Maunu CB1022 | 2025-05-09 09:01 | 45786.3757 | 2025-05-09 12:02 | 45786.5014 | 0.25836 | 0.0014274 | 93 | 16833 | Planned | Planned Interruption | New TX S264 not RFS due to weather - not yet connected to load side of L10219.
|  | O-6322-B | Ruatangata |  | Kamo CB6 | 2025-05-09 10:08 | 45786.4222 | 2025-05-09 12:38 | 45786.5264 | 0.22792 | 0.0015195 | 99 | 14850 | Planned | Planned Interruption | Replace existing pole with B12.5
|  | F-9751-A | Springs Flat |  | Kamo CB1 | 2025-05-09 15:03 | 45786.6271 | 2025-05-09 15:52 | 45786.6613 | 0.24511 | 0.015747 | 1026 | 15970 | Unplanned | Third Party Interference | FP 392939 Car vs pole - Recl 1555 & CB 1 both tripped. No damage to pole, Restored.
|  | F-9754-A | Awakino Point |  | Dargaville CB4 | 2025-05-10 20:09 | 45787.8399 | 2025-05-10 20:34 | 45787.857 | 0.1413 | 0.0057556 | 375 | 9206 | Unplanned | Unknown | FP 392957 - Patrolled & relivened
|  | O-18187-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-05-12 09:09 | 45789.3812 | 2025-05-12 13:21 | 45789.5563 | 0.042545 | 0.00016883 | 11 | 2772 | Planned | Planned Interruption | Remove X-arm mounted LAs and upgrade transformer C473 at Pole 310912
|  | O-6433-B | Tangowahine |  | Dargaville CB8 | 2025-05-12 09:30 | 45789.3961 | 2025-05-12 14:01 | 45789.5843 | 0.15387 | 0.00056789 | 37 | 10025 | Planned | Planned Interruption | Replace Poles 37347, 37351 & 334931 for future safe transport of high load (Raise Road crossing line height)
|  | F-9757-A | Access Rd |  | Ruawai CB1022 | 2025-05-12 13:37 | 45789.5674 | 2025-05-12 13:54 | 45789.5791 | 0.08328 | 0.005111 | 333 | 5426 | Unplanned | Unknown | A B C OC - No FPIs on SWs down fdr. Couldnt backfeed from SW 2077 upto SW 2235 due to Matakohe regs issue.
|  | F-235-B | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-05-12 17:39 | 45789.7354 | 2025-05-12 19:21 | 45789.8063 | 0.098628 | 0.00096694 | 63 | 6426 | Unplanned | Vegetation | 392992 Reparied damaged conductor
|  | O-6643-B | Ararua |  | Mareretu CB2 | 2025-05-13 09:10 | 45790.3819 | 2025-05-13 15:06 | 45790.6292 | 0.01056 | 3.0697e-05 | 2 | 688 | Planned | Planned Interruption | Replace HV & LV x-arms from pole 48687 to EOL
|  | O-6511-B | Tangowahine |  | Dargaville CB8 | 2025-05-13 09:33 | 45790.3977 | 2025-05-13 15:25 | 45790.6426 | 0.086579 | 0.00024557 | 16 | 5641 | Planned | Planned Interruption | Replace various poles for line height mitigation and install temp switch
|  | O-18145-A | Tangowahine |  | Dargaville CB8 | 2025-05-14 09:02 | 45791.3764 | 2025-05-14 12:47 | 45791.5326 | 0.12432 | 0.00055254 | 36 | 8100 | Planned | Planned Interruption | Pole, crossarms and harware replacements. V
|  | F-9763-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-05-14 09:03 | 45791.3771 | 2025-05-14 09:20 | 45791.3889 | 0.00052184 | 3.0697e-05 | 2 | 34 | Unplanned | Wildlife | FP 393027 - Found blown HV fuse, llarge rat on top of tx. Cleared and relivened. V
|  | F-9772-A | Access Rd |  | Ruawai CB1022 | 2025-05-14 20:52 | 45791.8695 | 2025-05-15 09:25 | 45792.3924 | 0.35499 | 0.0094085 | 893 | 23372 | Unplanned | Wildlife | 393054 / Trip B C & N. Found Swan Vs Lines causing lines down at pole 44806. Daylight patrol past L3220.
|  | O-6439-B | Thelma Road |  | Mangawhai North CB4 | 2025-05-15 09:05 | 45792.3785 | 2025-05-15 14:01 | 45792.584 | 0.8009 | 0.0028241 | 184 | 52182 | Planned | Planned Interruption | Replace Poles and hardware.
|  | O-18388-A | Turiwiri |  | Dargaville CB9 | 2025-05-15 09:13 | 45792.384 | 2025-05-15 14:08 | 45792.5889 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Replace Pole and Transformer. 2 ICPs not logged as Tx J306 replaced - to be edited
|  | O-6544-B | One Tree Point |  | Ruakaka CB6 | 2025-05-15 10:02 | 45792.4181 | 2025-05-15 13:21 | 45792.5563 | 0.6414 | 0.0032231 | 210 | 41790 | Planned | Planned Interruption | Pole replacement to allow high load transport. Repl KL5180.
|  | O-18379-A | Langs Beach |  | Mangawhai North CB3 | 2025-05-16 09:28 | 45793.3944 | 2025-05-16 11:54 | 45793.4958 | 0.011204 | 7.6741e-05 | 5 | 730 | Planned | Planned Interruption | Rectify high partial discharge on HV cables in TX MC455.
|  | O-18547-A | Coast |  | Dargaville CB6 | 2025-05-18 09:01 | 45795.3754 | 2025-05-18 14:05 | 45795.5868 | 0.1308 | 0.00042975 | 28 | 8522 | Planned | Planned Interruption | Pole replacements
|  | O-18391-A | Waipu |  | Ruakaka CB2 | 2025-05-19 09:02 | 45796.3766 | 2025-05-19 14:54 | 45796.6208 | 1.495 | 0.0042515 | 277 | 97407 | Planned | Planned Interruption | Urgent pole replacements.
|  | O-6370-B | Puwera |  | Maungatapere CB7 | 2025-05-20 09:01 | 45797.3757 | 2025-05-20 14:32 | 45797.6055 | 0.09651 | 0.00029162 | 19 | 6288 | Planned | Planned Interruption | Replace Poles and hardware
|  | O-18553-A | Titoki |  | Poroti CB1032 | 2025-05-20 12:07 | 45797.5049 | 2025-05-20 13:34 | 45797.5653 | 0.013353 | 0.00015348 | 10 | 870 | Planned | Planned Interruption | New TX P505 being installed
|  | O-6568-B | Coast |  | Dargaville CB6 | 2025-05-21 09:02 | 45798.3762 | 2025-05-21 15:23 | 45798.6407 | 0.29811 | 0.00078276 | 51 | 19423 | Planned | Planned Interruption | Pole changes & Tx relocation to allow transport of high loads
|  | O-6661-B | Ararua |  | Mareretu CB2 | 2025-05-21 09:22 | 45798.3903 | 2025-05-21 14:50 | 45798.6181 | 0.5437 | 0.0016576 | 108 | 35424 | Planned | Planned Interruption | replace poles, x-arms and hardware between Poles 308113 and Pole 48592
|  | O-18220-A | Hakaru |  | Kaiwaka CB1032 | 2025-05-23 09:04 | 45800.3777 | 2025-05-23 14:49 | 45800.6174 | 0.20129 | 0.00058323 | 38 | 13115 | Planned | Planned Interruption | Remove transformer MC428 and install pad mount in new location, labelled MC588
|  | O-18295-A | Swamp North |  | Hikurangi CB1042 | 2025-05-23 09:07 | 45800.3799 | 2025-05-23 12:55 | 45800.5382 | 0.14034 | 0.00069067 | 45 | 9144 | Planned | Planned Interruption | Upgrade one span of conductor to Upgrade Tx KB356 from 1ph to 3 phase
|  | F-9808-A | Swamp North |  | Hikurangi CB1042 | 2025-05-23 13:25 | 45800.559 | 2025-05-23 14:31 | 45800.6051 | 0.30273 | 0.0061853 | 403 | 19724 | Unplanned | Wildlife | FP393280 Reported bird strike at KB136, patrolled and livened.
|  | O-18238-A | Treatment |  | Kioreroa CB2 | 2025-05-25 09:03 | 45802.3771 | 2025-05-25 13:07 | 45802.5465 | 0.022378 | 9.209e-05 | 6 | 1458 | Planned | Planned Interruption | Installed new Recl 1558
|  | F-9814-A | Marsden South |  | Bream Bay CB1111 | 2025-05-26 15:09 | 45803.6312 | 2025-05-26 15:28 | 45803.6444 | 0.00029162 | 1.5348e-05 | 1 | 19 | Unplanned | Defective Equipment | FP 393317. Repair broken HV insulator
|  | F-9817-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-05-26 23:43 | 45803.9882 | 2025-05-27 00:55 | 45804.0382 | 0.045308 | 0.00062928 | 41 | 2952 | Unplanned | Defective Equipment | FP 393333 HV Jumper pole 49378
|  | O-6514-B | Mata |  | Ruakaka CB3 | 2025-05-27 09:10 | 45804.3817 | 2025-05-27 13:31 | 45804.5631 | 0.53704 | 0.0020567 | 134 | 34990 | Planned | Planned Interruption | Maintenance work - Poles and HV/LV ARM & HARDWARE REPLACEMENTS.
|  | O-18451-A | Hokianga Rd |  | Dargaville CB7 | 2025-05-27 10:04 | 45804.4194 | 2025-05-27 12:46 | 45804.5319 | 0.091997 | 0.00056789 | 37 | 5994 | Planned | Planned Interruption | Repair partial discharge damage on 11kV cables
|  | O-18196-A | Hakaru |  | Kaiwaka CB1032 | 2025-05-28 08:41 | 45805.3618 | 2025-05-28 11:40 | 45805.4861 | 0.0027473 | 1.5348e-05 | 1 | 179 | Planned | Planned Interruption | Replace Pole 45876 & various 11kV works on spur line
|  | O-6583-B | Coast |  | Dargaville CB6 | 2025-05-28 09:17 | 45805.3868 | 2025-05-28 14:36 | 45805.6083 | 0.28887 | 0.00090555 | 59 | 18821 | Planned | Planned Interruption | Pole upgrades for clearance for road transport
|  | F-9829-A | Taipuha |  | Mareretu CB1 | 2025-05-28 10:48 | 45805.45 | 2025-05-28 11:03 | 45805.4601 | 0.047349 | 0.0070448 | 459 | 3085 | Unplanned | Defective Equipment | Tripped B & C phase overcurrent. 15min close, All BTN. Blown jumper found on F-9844-A
|  | O-18181-A | Ararua |  | Mareretu CB2 | 2025-05-29 09:09 | 45806.3812 | 2025-05-29 14:30 | 45806.6042 | 0.12317 | 0.00038371 | 25 | 8025 | Planned | Planned Interruption | Replace poles, hardware and transformers like for like
|  | F-9832-A | Matapouri |  | Ngunguru CB1032 | 2025-05-29 10:35 | 45806.441 | 2025-05-29 15:27 | 45806.6438 | 0.27676 | 0.0029315 | 191 | 18032 | Unplanned | Defective Equipment | FP 393393 Replace DDOs NT193
|  | F-9838-A | North Dargaville |  | Dargaville CB1 | 2025-05-29 20:57 | 45806.8729 | 2025-05-29 21:11 | 45806.8827 | 0.041072 | 0.0030236 | 197 | 2676 | Unplanned | Unknown | 393418 / Trip & 15 Min close. A & N Phase Earth Fault.
|  | F-9841-A | Taipuha |  | Mareretu CB1 | 2025-05-30 01:36 | 45807.0667 | 2025-05-30 01:58 | 45807.0819 | 0.049913 | 0.0070448 | 459 | 3252 | Unplanned | Defective Equipment | Overcurrent B & C. blown jumper found on F-9844-A
|  | F-9844-A | Taipuha |  | Mareretu CB1 | 2025-05-30 03:13 | 45807.134 | 2025-05-30 05:29 | 45807.2285 | 0.035485 | 0.00026092 | 17 | 2312 | Unplanned | Defective Equipment | 393421 / Blown HV jumper at links 469 load side repaired & BTN
|  | F-9847-A | Whatatiri |  | Maungatapere CB8 | 2025-05-30 08:03 | 45807.3354 | 2025-05-30 10:25 | 45807.434 | 0.015256 | 0.00010744 | 7 | 994 | Unplanned | Vegetation | FP 393422 Trees on lines at pole 59920. HV fuses blown
|  | O-6622-B | Pataua |  | Parua Bay CB1 | 2025-05-30 09:02 | 45807.3764 | 2025-05-30 10:32 | 45807.4389 | 0.12217 | 0.0014274 | 93 | 7960 | Planned | Planned Interruption | Replacing Switch 9789 in the open position.
|  | O-18343-A | Tangowahine |  | Dargaville CB8 | 2025-05-30 09:04 | 45807.3778 | 2025-05-30 14:33 | 45807.6062 | 0.31307 | 0.00095159 | 62 | 20398 | Planned | Planned Interruption | Pole and X-arm replacements
|  | O-6121-B | Ararua |  | Mareretu CB2 | 2025-05-30 09:25 | 45807.3924 | 2025-05-30 14:44 | 45807.6139 | 0.13709 | 0.00042975 | 28 | 8932 | Planned | Planned Interruption | Replace x-arms, hardware & TX E259 like for like
|  | F-9850-A | North Dargaville |  | Dargaville CB1 | 2025-05-30 09:45 | 45807.4062 | 2025-05-30 12:05 | 45807.5035 | 0.060165 | 0.00042975 | 28 | 3920 | Unplanned | Unknown | FP 393424. Found 1 x blown fuse at L10099. Patrolled and livened. Unkown fault
|  | F-9865-A | Te Kopuru |  | Dargaville CB2 | 2025-05-31 23:46 | 45808.9903 | 2025-06-01 00:02 | 45809.0014 | 0.14188 | 0.014612 | 952 | 9244 | Unplanned | Unknown | Unknown - Trip OC Phase AB. FPI @ Sw 2255 (AB).
|  | F-9868-A | Mains Ave |  | Tikipunga CB2 | 2025-06-01 18:58 | 45809.7902 | 2025-06-01 19:30 | 45809.8122 | 0.63456 | 0.020874 | 1360 | 41344 | Unplanned | Third Party Interference | 393470/ Car v LV Pole, LV Lines down across road. Deenergised feeders for safety.
|  | F-9871-A | One Tree Point |  | Ruakaka CB6 | 2025-06-03 11:58 | 45811.4986 | 2025-06-03 12:50 | 45811.5347 | 0.090186 | 0.0017344 | 113 | 5876 | Unplanned | Defective Equipment | Repair crossarm following king bolt failure
|  | F-9874-A | Wairere |  | Mareretu CB5 | 2025-06-03 20:36 | 45811.8581 | 2025-06-03 20:52 | 45811.8693 | 0.090202 | 0.0080271 | 523 | 5877 | Unplanned | Unknown | Relivened remotely in sections - all restored
|  | O-6637-B | Te Hihi |  | Maunu CB1022 | 2025-06-04 09:02 | 45812.3762 | 2025-06-04 15:11 | 45812.6327 | 1.5587 | 0.0042208 | 275 | 101558 | Planned | Planned Interruption | Safe Transport of a High Load - Pole replacements. Slight Delay to re livening due to work load.
|  | F-9877-A | Maungakaramea |  | Maungatapere CB3 | 2025-06-04 15:21 | 45812.6398 | 2025-06-05 00:05 | 45813.0035 | 1.9132 | 0.0092396 | 602 | 124653 | Unplanned | Vegetation | FP 393533 - Replace HV cross arm. Hi/Low Clash. Delay to livening due to access issues.
|  | F-9880-A | Ruatangata |  | Kamo CB6 | 2025-06-04 19:21 | 45812.8061 | 2025-06-05 03:45 | 45813.1562 | 0.78334 | 0.011496 | 749 | 51038 | Unplanned | Vegetation | FP 393543 - Repair lines down
|  | O-18355-A | Waipu |  | Ruakaka CB2 | 2025-06-05 09:05 | 45813.3782 | 2025-06-05 12:40 | 45813.5276 | 0.91471 | 0.0042515 | 277 | 59597 | Planned | Planned Interruption | Clear trees around 11kv and lv lines from pole #10275 to pole #10278. Ran over time due to work load.
|  | O-18505-A | Bickerstaff |  | Maungaturoto CB2 | 2025-06-05 09:09 | 45813.3811 | 2025-06-05 15:09 | 45813.631 | 0.56874 | 0.0015809 | 103 | 37056 | Planned | Planned Interruption | Uprade Tx D120 and replace pole hardware
|  | O-18655-A | One Tree Point |  | Ruakaka CB6 | 2025-06-05 09:21 | 45813.3896 | 2025-06-05 15:00 | 45813.625 | 0.0052031 | 1.5348e-05 | 1 | 339 | Planned | Planned Interruption | Transformer Upgrade
|  | O-18457-A | Mangawhai Heads |  | Mangawhai North CB1 | 2025-06-06 09:16 | 45814.3861 | 2025-06-06 15:13 | 45814.634 | 0.26849 | 0.00075206 | 49 | 17493 | Planned | Planned Interruption | Install new RMU, remove fuses 4059 and re-configure MC310 to be connected to new RMU
|  | O-18658-A | One Tree Point |  | Ruakaka CB6 | 2025-06-06 09:25 | 45814.3924 | 2025-06-06 15:35 | 45814.6493 | 0.011358 | 3.0697e-05 | 2 | 740 | Planned | Planned Interruption | Transformer Upgrade
|  | F-9895-A | Maungakaramea |  | Maungatapere CB3 | 2025-06-07 18:54 | 45815.7873 | 2025-06-08 01:11 | 45816.0493 | 0.4158 | 0.0092396 | 929 | 27309 | Unplanned | Wildlife | Trip A, B & C. Overcurrent. Found Line down at pole 21859. Repaired & BTN
|  | F-9898-A | North Dargaville |  | Dargaville CB1 | 2025-06-07 20:12 | 45815.8413 | 2025-06-07 20:28 | 45815.8527 | 0.03834 | 0.0023329 | 152 | 2498 | Unplanned | Unknown | Trip & 15 minute close. B Phase. BTN
|  | O-18373-A | Awakino Point |  | Dargaville CB4 | 2025-06-08 09:00 | 45816.3752 | 2025-06-08 15:27 | 45816.6437 | 1.6139 | 0.0041747 | 272 | 105151 | Planned | Planned Interruption | Pole replacement
|  | F-9904-A | Coast |  | Dargaville CB6 | 2025-06-10 10:28 | 45818.4363 | 2025-06-10 10:48 | 45818.4503 | 0.23217 | 0.016054 | 1046 | 15127 | Unplanned | Unknown | A C phase OC. SCF @ SW 3137 restricted back feeding. Close >15min.
|  | F-9910-A | 2nd Ave |  | Alexander St CB3 | 2025-06-10 12:20 | 45818.514 | 2025-06-10 14:36 | 45818.6083 | 0.39876 | 0.016699 | 1088 | 25981 | Unplanned | Wildlife | FP 393705 - Lines down. Suspected bird strike, found feathers on other phase but couldn't locate bird.
|  | O-18340-A | Awakino Point |  | Dargaville CB4 | 2025-06-11 09:05 | 45819.3785 | 2025-06-11 15:57 | 45819.6646 | 0.60073 | 0.0014581 | 95 | 39140 | Planned | Planned Interruption | HV X-arm and Pole replacements
|  | F-9919-A | Te Kopuru |  | Dargaville CB2 | 2025-06-11 12:57 | 45819.5396 | 2025-06-11 13:07 | 45819.5465 | 0.00046045 | 4.6045e-05 | 3 | 30 | Unplanned | Defective Equipment | FP 393735 - Found 1x blown HV fuse. Fuse wire heavily corroded, removed reloaded and closed other 2x links.
|  | O-18787-A | Fert. Works |  | Kioreroa CB6 | 2025-06-11 14:36 | 45819.6083 | 2025-06-11 15:40 | 45819.6528 | 0.0098229 | 0.00015348 | 10 | 640 | Planned | Planned Interruption | New RMU installation
|  | F-9928-A | Awakino Point |  | Dargaville CB4 | 2025-06-11 21:27 | 45819.8937 | 2025-06-11 23:17 | 45819.9701 | 0.51558 | 0.0057556 | 375 | 33592 | Unplanned | Unknown | FP 393762. Checked sub and patrolled 11kV due to heavy fault. Nothing cause found. Restored.
|  | F-9931-A | Access Rd |  | Ruawai CB1022 | 2025-06-12 01:06 | 45820.0459 | 2025-06-12 01:23 | 45820.0574 | 0.028947 | 0.005111 | 333 | 1886 | Unplanned | Unknown | Sw 2156 B&C ph fault. Relivened remotely
|  | O-18817-A | One Tree Point |  | Ruakaka CB6 | 2025-06-12 09:35 | 45820.3993 | 2025-06-12 12:48 | 45820.5333 | 0.33473 | 0.0017344 | 113 | 21809 | Planned | Planned Interruption | Replace and relocatepole away from customer driveway
|  | F-9940-A | Turiwiri |  | Dargaville CB9 | 2025-06-12 12:34 | 45820.5236 | 2025-06-12 14:10 | 45820.5903 | 0.014734 | 0.00015348 | 10 | 960 | Unplanned | Defective Equipment | FP393780 Blown jumper at pole 47888
|  | F-9943-A | Tangaihi |  | Ruawai CB1032 | 2025-06-12 14:02 | 45820.5847 | 2025-06-12 14:04 | 45820.5858 | 0.014949 | 0.0098536 | 642 | 974 | Unplanned | Unknown | No fault number - CB 1032 closed and held Fault report left as HV incident due to time running over 1min
|  | O-18631-A | Bickerstaff |  | Maungaturoto CB2 | 2025-06-13 09:04 | 45821.3778 | 2025-06-13 14:51 | 45821.6188 | 0.11184 | 0.00032231 | 21 | 7287 | Planned | Planned Interruption | Pole hardware replacement and straightening Poles
|  | O-18676-A | Swamp South |  | Hikurangi CB1092 | 2025-06-13 09:05 | 45821.3784 | 2025-06-13 15:06 | 45821.6294 | 0.10543 | 0.00029162 | 19 | 6869 | Planned | Planned Interruption | Replacing 11kv Cross arms & re-sagging 11kv Replacing 11kv Fuses 6119
|  | O-18970-A | North Dargaville |  | Dargaville CB1 | 2025-06-13 10:12 | 45821.425 | 2025-06-13 10:32 | 45821.4389 | 0.008595 | 0.00042975 | 28 | 560 | Planned | Planned Interruption | Replacing Solid Links with Reclosing Links
|  | F-9946-A | North Dargaville |  | Dargaville CB1 | 2025-06-13 13:23 | 45821.5576 | 2025-06-13 15:07 | 45821.6299 | 0.083003 | 0.00079811 | 52 | 5408 | Unplanned | Defective Equipment | TC4120562 - in conjunction O-18970-A Replacing HV fuse holder as damage found during replacement of links for reclosing links
|  | F-9955-A | Alamein Ave |  | Onerahi CB3 | 2025-06-15 03:06 | 45823.1289 | 2025-06-15 05:58 | 45823.2486 | 1.8467 | 0.02488 | 1621 | 120321 | Unplanned | Defective Equipment | 393828 / Tripped & patrolled lines. Established UG fault between Sw 10089 & 9447.
|  | F-9958-A | Coast |  | Dargaville CB6 | 2025-06-16 21:55 | 45824.9132 | 2025-06-16 22:13 | 45824.9254 | 0.090739 | 0.016054 | 1046 | 5912 | Unplanned | Unknown | Tripped B&C phase O/C - Unknown cause, Sw10009 FPI's activated - Closed after 15mins
|  | O-18532-A | Okara Drive |  | Whangarei South CB1092 | 2025-06-17 07:04 | 45825.2944 | 2025-06-17 08:18 | 45825.3458 | 0.042024 | 0.00056789 | 37 | 2738 | Planned | Planned Interruption | Remove 11kV Cable from Crucifix at pole 27993 - RMU upgrade
|  | O-18490-A | Mangawhai Heads |  | Mangawhai North CB1 | 2025-06-17 08:38 | 45825.3597 | 2025-06-17 16:13 | 45825.6757 | 1.4524 | 0.0034687 | 226 | 94632 | Planned | Planned Interruption | Upgrade Transformer and replace poles - job ran overtime
|  | O-18508-A | Tamaterau |  | Onerahi CB7 | 2025-06-17 09:19 | 45825.3882 | 2025-06-17 14:57 | 45825.6229 | 0.67959 | 0.0020106 | 131 | 44278 | Planned | Planned Interruption | Install new automated Switch 10287
|  | O-18535-A | Okara Drive |  | Whangarei South CB1092 | 2025-06-17 23:32 | 45825.9806 | 2025-06-18 03:35 | 45826.1493 | 0.085781 | 0.00035301 | 23 | 5589 | Planned | Planned Interruption | Move 11KV cable from SW204 to SW10239 Replacement RMU
|  | O-18400-A | Taipuha |  | Mareretu CB1 | 2025-06-18 09:04 | 45826.3778 | 2025-06-18 13:37 | 45826.5674 | 0.37711 | 0.0013813 | 90 | 24570 | Planned | Planned Interruption | Replace Pole/Crossarms and Fit Temp Fuses
|  | O-18964-A | Hakaru |  | Kaiwaka CB1032 | 2025-06-19 10:09 | 45827.4229 | 2025-06-19 15:58 | 45827.6653 | 0.0053565 | 1.5348e-05 | 1 | 349 | Planned | Planned Interruption | Replace pole hardware on spur line
|  | F-9964-A | Titoki |  | Poroti CB1032 | 2025-06-20 17:39 | 45828.7352 | 2025-06-20 17:54 | 45828.7458 | 0.10139 | 0.011834 | 771 | 6606 | Unplanned | Unknown | Trip Overcurrent. Close CB 1032 Titoki 15 mins. BTN
|  | O-18418-A | Coast |  | Dargaville CB6 | 2025-06-23 08:35 | 45831.3576 | 2025-06-23 16:47 | 45831.6993 | 0.11327 | 0.00023022 | 15 | 7380 | Planned | Planned Interruption | Install 66kV poles and liven new Transformer M582
|  | O-6226-B | Ararua |  | Mareretu CB2 | 2025-06-24 09:26 | 45832.3932 | 2025-06-24 14:33 | 45832.6062 | 1.3137 | 0.0042822 | 279 | 85593 | Planned | Planned Interruption | Network Maintenance - replace x-arms, pole and transformers E114, E256 like for like
|  | F-9979-A | Coast |  | Dargaville CB6 | 2025-06-25 03:56 | 45833.1641 | 2025-06-25 04:12 | 45833.1751 | 0.11639 | 0.016054 | 1046 | 7583 | Unplanned | Unknown | B&C phase O/C, Sw 2025 FPI's activated, Closed after 15mins - Unknown cause
|  | O-18541-A | Okara Drive |  | Whangarei South CB1092 | 2025-06-25 07:20 | 45833.3058 | 2025-06-25 08:24 | 45833.3503 | 0.036345 | 0.00056789 | 37 | 2368 | Planned | Planned Interruption | Complete installation of new RMU 10238 - reinstate Temp Break
|  | O-18586-A | Tamaterau |  | Onerahi CB7 | 2025-06-25 09:01 | 45833.3757 | 2025-06-25 15:49 | 45833.659 | 1.3839 | 0.003392 | 221 | 90168 | Planned | Planned Interruption | Replacing 11kv & 400v Poles & Cross arms. Installing temp switch at pole 51741 for work in area coming up
|  | O-18865-A | Bickerstaff |  | Maungaturoto CB2 | 2025-06-25 09:08 | 45833.3806 | 2025-06-25 13:41 | 45833.5701 | 0.18436 | 0.00067532 | 44 | 12012 | Planned | Planned Interruption | Straighten poles, replace hardware and upgrade TX D209
|  | O-18889-A | Coast |  | Dargaville CB6 | 2025-06-26 08:41 | 45834.3618 | 2025-06-26 16:02 | 45834.6681 | 0.081223 | 0.00018418 | 12 | 5292 | Planned | Planned Interruption | Install 66KV Poles, Remove TX M125, Install and liven Tx M581. Please alter number of Customers off, should be 15.
|  | O-18940-A | Cairnfield Rd |  | Tikipunga CB5 | 2025-06-26 09:04 | 45834.3778 | 2025-06-26 10:31 | 45834.4382 | 0.086794 | 0.00099764 | 65 | 5655 | Planned | Planned Interruption | Top up oil on Tx WC170
|  | O-18898-A | Ararua |  | Mareretu CB2 | 2025-06-26 09:29 | 45834.3951 | 2025-06-26 13:18 | 45834.5542 | 0.11599 | 0.00050649 | 33 | 7557 | Planned | Planned Interruption | Replace pole hardware
|  | F-9994-A | North Dargaville |  | Dargaville CB1 | 2025-06-26 10:47 | 45834.4495 | 2025-06-26 11:48 | 45834.4914 | 0.14079 | 0.0023329 | 152 | 9173 | Unplanned | Unknown | 394118/ Trip Phase B/EF. Intermittent Fault, Line Patrol carried out
|  | F-9997-A | Bickerstaff |  | Maungaturoto CB2 | 2025-06-27 07:27 | 45835.3103 | 2025-06-27 07:49 | 45835.3256 | 0.18099 | 0.010345 | 674 | 11792 | Unplanned | Adverse Weather | 394139/ trip OC Phase A/B. FPIs 349476
|  | O-18580-A | Walton St |  | Whangarei South CB1022 | 2025-06-29 08:32 | 45837.3556 | 2025-06-29 16:03 | 45837.6687 | 2.4345 | 0.0054179 | 353 | 158618 | Planned | Planned Interruption | - Replace pole & raise LV road crossings. - Replace SW 9270 with SW10279 - Replace SW 7275 with SW10280
|  | O-18550-A | Golden Bay Nth |  | Maungatapere POS CB1332 | 2025-06-29 14:03 | 45837.5854 | 2025-06-29 16:22 | 45837.6819 | 0.26241 | 0.0018878 | 123 | 17097 | Planned | Planned Interruption | Replave 33kV Cross-arm. Note: time off in S-113-B, time on S-112-B (step 39)
|  | O-19192-A | Springs Flat |  | Kamo CB1 | 2025-06-30 09:03 | 45838.3771 | 2025-06-30 13:27 | 45838.5604 | 0.012156 | 4.6045e-05 | 3 | 792 | Planned | Planned Interruption | Upgrade transformer KS418
|  | O-18724-A | Pataua |  | Parua Bay CB1 | 2025-06-30 09:56 | 45838.4139 | 2025-06-30 13:40 | 45838.5694 | 0.13752 | 0.00061393 | 40 | 8960 | Planned | Planned Interruption | LV MAINTENANCE TO REPLACE LV CONDUCTOR & HARDWARE
|  | O-18916-A | Whatatiri |  | Maungatapere CB8 | 2025-07-01 09:08 | 45839.3806 | 2025-07-01 15:09 | 45839.6315 | 0.51576 | 0.0014274 | 93 | 33604 | Planned | Planned Interruption | Pole replacements
|  | O-18766-A | Whakapara |  | Hikurangi CB1112 | 2025-07-01 09:33 | 45839.3979 | 2025-07-01 12:21 | 45839.5146 | 0.78644 | 0.0046812 | 305 | 51240 | Planned | Planned Interruption | Tree Clearing Work
|  | O-18886-A | Coast |  | Dargaville CB6 | 2025-07-02 08:39 | 45840.3606 | 2025-07-02 17:28 | 45840.7278 | 0.064938 | 0.00012279 | 8 | 4231 | Planned | Planned Interruption | Replace Transformer and install 66kV poles
|  | O-6601-B | Austin Road |  | Maunu CB1072 | 2025-07-02 09:02 | 45840.3764 | 2025-07-02 15:53 | 45840.6618 | 0.35326 | 0.0008595 | 56 | 23016 | Planned | Planned Interruption | Pole replacement - Future Safe Transport of a High Load (GEN on S139)
|  | F-10009-A | North Dargaville |  | Dargaville CB1 | 2025-07-02 16:50 | 45840.7015 | 2025-07-02 21:12 | 45840.8834 | 0.2552 | 0.0030236 | 197 | 16627 | Unplanned | Vegetation | 394295 Fallen tree on lines between poles 26535 and 26534
|  | F-10012-A | Montgomery Ave |  | Onerahi CB8 | 2025-07-03 02:34 | 45841.1073 | 2025-07-03 02:51 | 45841.1185 | 0.14435 | 0.015962 | 1040 | 9405 | Unplanned | Adverse Weather | Feeder tripped on ABC over-current, all > 1000A. FPIs picked up at SW938. Opened and closed CB. Closed 938 after 15 min, held
|  | F-250-B | Montgomery Ave |  | Onerahi CB8 | 2025-07-03 04:56 | 45841.2052 | 2025-07-03 12:56 | 45841.5389 | 0.25105 | 0.017436 | 1136 | 16357 | Unplanned | Vegetation | FP 394300 - Line patrolled Trees cleared
|  | O-19021-A | Western Hills Dr |  | Alexander St CB7 | 2025-07-03 09:15 | 45841.3854 | 2025-07-03 13:33 | 45841.5646 | 0.41182 | 0.0015962 | 104 | 26832 | Planned | Planned Interruption | HV Isolation for LV Work
|  | O-18985-A | Coast |  | Dargaville CB6 | 2025-07-03 09:55 | 45841.4135 | 2025-07-03 17:04 | 45841.7114 | 0.14483 | 0.00033766 | 22 | 9436 | Planned | Planned Interruption | Replace poles & install 66KV poles, Remove L10033 install L10288, Tree clearing. Late start due to faulty Sw 2086 & reconfig
|  | F-10024-A | Paranui |  | Tikipunga CB6 | 2025-07-03 14:33 | 45841.6062 | 2025-07-03 15:08 | 45841.6306 | 0.0013813 | 0.00055254 | 36 | 90 | Unplanned | Vegetation | FP 394318 - Isolate Tx for safety to replace LV fuse - found OH line twisted
|  | F-10027-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-07-03 16:38 | 45841.6932 | 2025-07-03 17:05 | 45841.7118 | 0.018894 | 0.00070602 | 46 | 1231 | Unplanned | Adverse Weather | FP 394324 - blown HV Fuses 418
|  | F-10030-A | Tangaihi |  | Ruawai CB1032 | 2025-07-03 18:52 | 45841.7858 | 2025-07-03 20:07 | 45841.8379 | 0.058707 | 0.00078276 | 51 | 3825 | Unplanned | Defective Equipment | 394337 Blown HV jumper
|  | O-19081-A | Turiwiri |  | Dargaville CB9 | 2025-07-04 10:04 | 45842.4193 | 2025-07-04 13:56 | 45842.5805 | 0.18516 | 0.00079811 | 52 | 12064 | Planned | Planned Interruption | Pole Maintainace and Fit HV Fuses
|  | O-6700-B | MPE-KEN 110kV Circuit 1 |  | Maungatapere POS CB342 | 2025-07-04 23:12 | 45842.9667 | 2025-07-05 00:13 | 45843.009 | 21.5916 | 0.46858 | 31618 | 1406778 | Unplanned | Lightning | 394455 MPE TP CB's Auto reclosed. Loss of KEN sub & lost comms. Tech switched. DC-DC converter faulty. Temp repair
|  | F-10045-A | Paparoa |  | Mareretu CB6 | 2025-07-05 07:02 | 45843.2932 | 2025-07-05 13:53 | 45843.5785 | 0.82531 | 0.015686 | 1022 | 53772 | Unplanned | Defective Equipment | FP 394458 - Repaired broken 11kV lines.
|  | F-10039-A | Tangaihi |  | Ruawai CB1032 | 2025-07-05 07:36 | 45843.3166 | 2025-07-05 13:39 | 45843.5691 | 1.7237 | 0.01125 | 733 | 112303 | Unplanned | Third Party Interference | 394459 Car vs pole 29407.
|  | F-10060-A | Maungakaramea |  | Maungatapere CB3 | 2025-07-05 12:56 | 45843.5386 | 2025-07-05 14:49 | 45843.6174 | 0.0046659 | 4.6045e-05 | 135 | 317 | Unplanned | Defective Equipment | 394462 Jumper off HV bushing at X127. Recl 1530 AR during fault finding
|  | F-10069-A | Whau Valley |  | Tikipunga CB1 | 2025-07-06 00:10 | 45844.0069 | 2025-07-06 06:18 | 45844.2625 | 0.25982 | 0.00070602 | 46 | 16928 | Unplanned | Defective Equipment | 39940 - Isolate Tx to repair cable
|  | O-19681-A | Ruatangata |  | Kamo CB6 | 2025-07-07 10:00 | 45845.4167 | 2025-07-07 11:29 | 45845.4785 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Level D-Sub
|  | O-19006-A | Coast |  | Dargaville CB6 | 2025-07-08 08:34 | 45846.3569 | 2025-07-08 17:29 | 45846.7285 | 0.10675 | 0.00019953 | 13 | 6955 | Planned | Planned Interruption | Conductor Installation - Delay on restoration, heavy conductor took longer than expected to install
|  | O-19009-A | Poroti |  | Maungatapere CB2 | 2025-07-08 09:07 | 45846.38 | 2025-07-08 13:04 | 45846.5445 | 0.61431 | 0.0025939 | 169 | 40025 | Planned | Planned Interruption | Replace various poles and pole hardware
|  | O-19327-A | Ararua |  | Mareretu CB2 | 2025-07-08 09:10 | 45846.382 | 2025-07-08 12:52 | 45846.5363 | 1.5661 | 0.0070448 | 459 | 102036 | Planned | Planned Interruption | Replace HV Crossarms
|  | F-10090-A | POR - WAI - MPEN |  | Maungatapere POS CB1312 | 2025-07-08 21:28 | 45846.8945 | 2025-07-08 21:44 | 45846.9055 | 0.33131 | 0.021058 | 1372 | 21586 | Unplanned | Unknown | CB 1312 MPE trip EF. F4. 15 min line Closed in & BTN
|  | O-19075-A | Tangowahine |  | Dargaville CB8 | 2025-07-09 09:03 | 45847.3771 | 2025-07-09 12:37 | 45847.5257 | 0.045983 | 0.00021488 | 14 | 2996 | Planned | Planned Interruption | Replacing 11kv Poles and Cross arms
|  | O-19267-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-09 09:06 | 45847.3792 | 2025-07-09 13:17 | 45847.5535 | 0.080901 | 0.00032231 | 21 | 5271 | Planned | Planned Interruption | Replace pole hardware at various sites
|  | O-19018-A | Otonga |  | Hikurangi CB1032 | 2025-07-09 09:21 | 45847.3894 | 2025-07-09 13:29 | 45847.5615 | 0.091307 | 0.00036836 | 24 | 5949 | Planned | Planned Interruption | Maintain Dsubs KS237 and KS210
|  | O-19024-A | Beach Road |  | Onerahi CB2 | 2025-07-10 09:06 | 45848.3792 | 2025-07-10 14:58 | 45848.6236 | 1.0805 | 0.0030697 | 200 | 70400 | Planned | Planned Interruption | Multiple Pole and hardware replacements
|  | O-19234-A | North Dargaville |  | Dargaville CB1 | 2025-07-10 09:32 | 45848.3974 | 2025-07-10 12:59 | 45848.541 | 0.2887 | 0.0013967 | 91 | 18810 | Planned | Planned Interruption | Remove Transformer M559 and Various poles from network
|  | O-19180-A | Otonga |  | Hikurangi CB1032 | 2025-07-10 09:33 | 45848.3979 | 2025-07-10 13:16 | 45848.5528 | 0.088989 | 0.00039905 | 26 | 5798 | Planned | Planned Interruption | Tree Clearing Work
|  | O-19030-A | Coast |  | Dargaville CB6 | 2025-07-11 08:37 | 45849.359 | 2025-07-11 15:51 | 45849.6604 | 0.086595 | 0.00019953 | 13 | 5642 | Planned | Planned Interruption | Installation of 66kv condutor
|  | O-18883-A | Jordan Valley |  | Hikurangi CB1102 | 2025-07-11 09:00 | 45849.3753 | 2025-07-11 11:47 | 45849.4909 | 0.10471 | 0.00062928 | 41 | 6822 | Planned | Planned Interruption | Tree Clearing Work
|  | O-19060-A | Taipuha |  | Mareretu CB1 | 2025-07-11 09:32 | 45849.3976 | 2025-07-11 13:07 | 45849.5462 | 0.24642 | 0.0011511 | 75 | 16055 | Planned | Planned Interruption | Replace HV and LV Hardware.
|  | F-10108-A | Kensington |  | Alexander St CB8 | 2025-07-11 20:03 | 45849.8353 | 2025-07-12 02:54 | 45850.121 | 0.22098 | 0.00053719 | 35 | 14398 | Unplanned | Third Party Interference | 394639 Car V Pole. Event P063136369. Pole labelled 903142 in field, labelled 332257 in ADMS/GIS
|  | F-10126-A | Taipuha |  | Mareretu CB1 | 2025-07-11 23:52 | 45849.9947 | 2025-07-12 00:09 | 45850.0063 | 0.041072 | 0.0070909 | 462 | 2676 | Unplanned | Unknown | Trip OC Phase BC. FPIs Sw 364 Phase BC.
|  | F-10135-A | Access Rd |  | Ruawai CB1022 | 2025-07-12 10:50 | 45850.4515 | 2025-07-12 11:06 | 45850.4623 | 0.036007 | 0.005111 | 333 | 2346 | Unplanned | Unknown | FPI's at 2156 activated
|  | F-10141-A | Langs Beach |  | Mangawhai North CB3 | 2025-07-12 22:52 | 45850.9527 | 2025-07-13 04:40 | 45851.1946 | 1.0291 | 0.012355 | 805 | 67049 | Unplanned | Third Party Interference | FP394651 Car vs pole Cove Rd MWI. FENZ F4251374 - Pole replacement delayed by Serious Crash Investigation.
|  | O-19003-A | ToeToe Rd |  | Kioreroa CB7 | 2025-07-13 09:08 | 45851.3806 | 2025-07-13 15:57 | 45851.6646 | 0.47081 | 0.0011511 | 75 | 30675 | Planned | Planned Interruption | Pole replacements
|  | O-19033-A | Coast |  | Dargaville CB6 | 2025-07-14 08:32 | 45852.3556 | 2025-07-14 19:15 | 45852.8021 | 0.1283 | 0.00019953 | 13 | 8359 | Planned | Planned Interruption | Improvements in Supply Quality: Install 66KV conductor
|  | O-19312-A | Ararua |  | Mareretu CB2 | 2025-07-14 09:15 | 45852.3854 | 2025-07-14 14:39 | 45852.6104 | 0.54204 | 0.001673 | 109 | 35316 | Planned | Planned Interruption | Straighten poles and re-sag conductor
|  | O-18571-A | Waipu |  | Ruakaka CB2 | 2025-07-14 09:32 | 45852.3972 | 2025-07-14 13:11 | 45852.5493 | 0.18151 | 0.00082881 | 54 | 11826 | Planned | Planned Interruption | Replace pole 10387 with B11 pole
|  | O-19369-A | Thelma Road |  | Mangawhai North CB4 | 2025-07-14 10:12 | 45852.425 | 2025-07-14 14:51 | 45852.6188 | 0.12418 | 0.0004451 | 29 | 8091 | Planned | Planned Interruption | Upgrade Transformer MC442
|  | O-19780-A | Cartwright Rd |  | Onerahi CB6 | 2025-07-15 09:12 | 45853.3833 | 2025-07-15 16:09 | 45853.6729 | 0.75449 | 0.002778 | 181 | 49158 | Planned | Planned Interruption | Network Maintenance - HV/LV POLE, ARM & HARDWARE REPLACEMENTS Remove Knifelinks 9407KL & 9509KL
|  | O-19141-A | Titoki |  | Poroti CB1032 | 2025-07-15 09:38 | 45853.4011 | 2025-07-15 13:52 | 45853.5776 | 0.050726 | 0.00019953 | 13 | 3305 | Planned | Planned Interruption | HV and LV croassarm replacements
|  | F-256-B | Turiwiri |  | Dargaville CB9 | 2025-07-15 13:01 | 45853.5424 | 2025-07-15 13:53 | 45853.5785 | 0.0023943 | 4.6045e-05 | 3 | 156 | Unplanned | Lightning | 394707/ x2 Blown HV Fuses
|  | F-259-B | Ararua |  | Mareretu CB2 | 2025-07-15 14:40 | 45853.6113 | 2025-07-15 15:18 | 45853.6378 | 0.26548 | 0.0069681 | 454 | 17297 | Unplanned | Third Party Interference | 394719 / Lines down reported after tripping due to shed roof. De Energised for safety. Found it to be LV lines
|  | F-262-B | Whangarei Heads |  | Parua Bay CB3 | 2025-07-15 15:58 | 45853.6653 | 2025-07-15 18:34 | 45853.7736 | 0.014366 | 9.209e-05 | 6 | 936 | Unplanned | Vegetation | 394721 / fuses x 2 blown from trees. Isolate for safety to clear trees from LV lines.
|  | F-10171-A | Taipuha |  | Mareretu CB1 | 2025-07-15 18:42 | 45853.7792 | 2025-07-15 19:16 | 45853.8028 | 0.0088713 | 0.00026092 | 17 | 578 | Unplanned | Defective Equipment | 394712 - Repaired broken jumper at Fuses 469
|  | F-10174-A | Tangowahine |  | Dargaville CB8 | 2025-07-15 18:57 | 45853.7896 | 2025-07-15 19:17 | 45853.8035 | 0.0012279 | 6.1393e-05 | 4 | 80 | Unplanned | Lightning | 394726 2x blown HV fuses
|  | O-18733-A | Otonga |  | Hikurangi CB1032 | 2025-07-16 09:04 | 45854.3778 | 2025-07-16 13:14 | 45854.5514 | 0.19569 | 0.00078276 | 51 | 12750 | Planned | Planned Interruption | Refurbish Transformers and pole hardware
|  | O-19291-A | Coast |  | Dargaville CB6 | 2025-07-16 09:12 | 45854.3833 | 2025-07-16 14:08 | 45854.5889 | 0.29076 | 0.00098229 | 64 | 18944 | Planned | Planned Interruption | HV isolation for LV repairs
|  | O-19300-A | Thelma Road |  | Mangawhai North CB4 | 2025-07-16 09:13 | 45854.384 | 2025-07-16 13:31 | 45854.5632 | 0.25739 | 0.00099764 | 65 | 16770 | Planned | Planned Interruption | Replace RMU
|  | O-19042-A | Mata |  | Ruakaka CB3 | 2025-07-16 09:31 | 45854.3967 | 2025-07-16 13:20 | 45854.5558 | 0.47133 | 0.0020567 | 134 | 30709 | Planned | Planned Interruption | Replace Pole 21410
|  | O-19324-A | Springs Flat |  | Kamo CB1 | 2025-07-17 09:02 | 45855.3764 | 2025-07-17 11:17 | 45855.4701 | 0.41233 | 0.0030543 | 199 | 26865 | Planned | Planned Interruption | HV isolation for tree clearing work
|  | F-10189-A | Jordan Valley |  | Hikurangi CB1102 | 2025-07-17 15:45 | 45855.6562 | 2025-07-17 16:00 | 45855.6666 | 0.10943 | 0.0073365 | 478 | 7130 | Unplanned | Adverse Weather | O/C B,C Phase. Close >15min
|  | F-10192-A | Coast |  | Dargaville CB6 | 2025-07-17 15:52 | 45855.6611 | 2025-07-17 18:53 | 45855.7869 | 0.97762 | 0.03857 | 2513 | 63696 | Unplanned | Defective Equipment | FP 394790 Rusted LA touching DDOs.
|  | F-10195-A | Whatatiri |  | Maungatapere CB8 | 2025-07-17 16:13 | 45855.6758 | 2025-07-17 16:29 | 45855.6865 | 0.14466 | 0.0093931 | 612 | 9425 | Unplanned | Adverse Weather | O/C Phase A,B,C .
|  | F-10198-A | Turiwiri |  | Dargaville CB9 | 2025-07-17 16:19 | 45855.6799 | 2025-07-17 23:33 | 45855.9812 | 0.97087 | 0.0098536 | 642 | 63256 | Unplanned | Adverse Environment | 394818 / Leaning pole 22370
|  | F-10204-A | Otonga |  | Hikurangi CB1032 | 2025-07-17 16:24 | 45855.6836 | 2025-07-17 16:40 | 45855.6941 | 0.078307 | 0.0091629 | 597 | 5102 | Unplanned | Adverse Weather | O/C Phase A,B.
|  | F-10210-A | Tangowahine |  | Dargaville CB8 | 2025-07-17 16:29 | 45855.6869 | 2025-07-18 01:15 | 45856.0521 | 1.2716 | 0.012739 | 830 | 82848 | Unplanned | Defective Equipment | 394834 / Broken Binder Pole 36801.
|  | F-10213-A | Tangaihi |  | Ruawai CB1032 | 2025-07-17 16:32 | 45855.6888 | 2025-07-17 16:59 | 45855.7076 | 0.26637 | 0.0098536 | 642 | 17355 | Unplanned | Adverse Weather | Trip O/C - Unknown
|  | F-10216-A | Paranui |  | Tikipunga CB6 | 2025-07-17 16:40 | 45855.6947 | 2025-07-18 10:21 | 45856.4313 | 1.5865 | 0.011373 | 741 | 103369 | Unplanned | Vegetation | FP: 394805. Pole 51311 snapped due to tree across line
|  | F-10219-A | Taipuha |  | Mareretu CB1 | 2025-07-17 16:43 | 45855.6966 | 2025-07-17 19:25 | 45855.8087 | 0.2879 | 0.014182 | 924 | 18758 | Unplanned | Adverse Weather | FPIs Sw 364 Phase A,B Wait and close
|  | F-10222-A | Matapouri |  | Ngunguru CB1032 | 2025-07-17 16:44 | 45855.6972 | 2025-07-17 17:04 | 45855.7113 | 0.24708 | 0.012171 | 793 | 16098 | Unplanned | Adverse Weather | O/C trip. 15min wait and close
|  | F-10225-A | Whangarei Heads |  | Parua Bay CB3 | 2025-07-17 16:45 | 45855.6979 | 2025-07-17 17:08 | 45855.7139 | 0.10856 | 0.012248 | 798 | 7073 | Unplanned | Adverse Weather | O/C Phase A,B Wait and close
|  | F-10228-A | Access Rd |  | Ruawai CB1022 | 2025-07-17 16:56 | 45855.7053 | 2025-07-17 18:22 | 45855.7653 | 0.16361 | 0.005111 | 333 | 10660 | Unplanned | Adverse Weather | O/C Wait and and close
|  | F-10234-A | Ararua |  | Mareretu CB2 | 2025-07-17 17:02 | 45855.7097 | 2025-07-18 15:13 | 45856.634 | 8.8756 | 0.011941 | 778 | 578281 | Unplanned | Defective Equipment | FP 394841 - Multpile faults. Broken x-arm @ Pole 48469. Lines down @ Pole 48704. Broken guy wire @ Pole 76717.
|  | F-10240-A | Paparoa |  | Mareretu CB6 | 2025-07-17 17:15 | 45855.7189 | 2025-07-17 19:20 | 45855.8059 | 1.1385 | 0.0090862 | 592 | 74178 | Unplanned | Defective Equipment | Reported Lines down, LV made safe and Livened
|  | F-10207-A | Te Kopuru |  | Dargaville CB2 | 2025-07-17 17:28 | 45855.7278 | 2025-07-18 10:28 | 45856.4361 | 1.0981 | 0.0074746 | 487 | 71543 | Unplanned | Defective Equipment | FP 394792. Lines down on fence
|  | F-10246-A | Wairere |  | Mareretu CB5 | 2025-07-17 17:41 | 45855.737 | 2025-07-17 21:32 | 45855.8971 | 1.6841 | 0.0080271 | 523 | 109725 | Unplanned | Defective Equipment | 394839/ Broken staywire around HV
|  | F-10249-A | Swamp North |  | Hikurangi CB1042 | 2025-07-17 18:01 | 45855.7506 | 2025-07-17 18:37 | 45855.7755 | 0.096786 | 0.006216 | 405 | 6306 | Unplanned | Adverse Weather | O/C FPIs Sw 672 B,C phase. Wait and close
|  | F-10264-A | Whakapara |  | Hikurangi CB1112 | 2025-07-17 18:14 | 45855.7595 | 2025-07-18 18:49 | 45856.784 | 0.6789 | 0.0018878 | 123 | 44233 | Unplanned | Defective Equipment | 394832 3x HV lines down, Helicopter needed to re-run span
|  | F-10267-A | Ararua |  | Mareretu CB2 | 2025-07-17 21:22 | 45855.8903 | 2025-07-17 21:42 | 45855.9043 | 0.044725 | 0.0022101 | 144 | 2914 | Unplanned | Adverse Weather | Trip Phase ABC - Unknown
|  | F-265-B | North River |  | Ruakaka CB7 | 2025-07-17 21:25 | 45855.8924 | 2025-07-18 09:18 | 45856.3875 | 0.010943 | 1.5348e-05 | 1 | 713 | Unplanned | Defective Equipment | FP 394825. HV jumper blown off
|  | F-10270-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-07-17 22:43 | 45855.9467 | 2025-07-18 15:35 | 45856.6493 | 1.0638 | 0.017773 | 1158 | 69312 | Unplanned | Defective Equipment | FP 394865 - Replace faulty RMU
|  | F-10273-A | Te Kopuru |  | Dargaville CB2 | 2025-07-18 07:30 | 45856.3124 | 2025-07-18 12:13 | 45856.509 | 0.36075 | 0.0030697 | 200 | 23504 | Unplanned | Defective Equipment | FP 394882 - replaced broken insulator
|  | F-10306-A | Te Kopuru |  | Dargaville CB2 | 2025-07-18 15:08 | 45856.6306 | 2025-07-18 22:53 | 45856.9534 | 0.19122 | 0.00099764 | 65 | 12459 | Unplanned | Defective Equipment | 394863 Broken HV Xarm @ Pole15892, Broken stay wire @ L265
|  | F-10315-A | Coast |  | Dargaville CB6 | 2025-07-19 20:12 | 45857.8415 | 2025-07-19 20:34 | 45857.8573 | 0.054778 | 0.0024097 | 157 | 3569 | Unplanned | Unknown | 394946 Closed in and held once on site - Unknown cause
|  | O-19219-A | Montgomery Ave |  | Onerahi CB8 | 2025-07-20 09:06 | 45858.3792 | 2025-07-20 12:20 | 45858.5139 | 0.25012 | 0.0012893 | 84 | 16296 | Planned | Planned Interruption | Pole hardware replacements
|  | F-10324-A | Coast |  | Dargaville CB6 | 2025-07-20 18:50 | 45858.7846 | 2025-07-21 00:12 | 45859.0083 | 0.36599 | 0.047641 | 3104 | 23846 | Unplanned | Wildlife | FP 394980. Swan clash @ pole 301151. Additional 35 customers shutdown on CB 1 due to Sw 2086 faulty (cant be used as isolation)
|  | O-19036-A | Coast |  | Dargaville CB6 | 2025-07-21 08:31 | 45859.3551 | 2025-07-21 16:45 | 45859.6981 | 0.21985 | 0.0004451 | 29 | 14324 | Planned | Planned Interruption | Replace Poles SH12 and Install Conductor
|  | O-19378-A | Mangawhai Heads |  | Mangawhai North CB1 | 2025-07-21 09:03 | 45859.3771 | 2025-07-21 15:22 | 45859.6403 | 1.6229 | 0.0042822 | 279 | 105741 | Planned | Planned Interruption | Pole and hardware replacements - delay on restoration due to pole hole issue
|  | F-10339-A | Swamp North |  | Hikurangi CB1042 | 2025-07-22 00:05 | 45860.0035 | 2025-07-22 00:21 | 45860.0147 | 0.076051 | 0.006216 | 405 | 4955 | Unplanned | Unknown | 15 min liven
|  | O-19045-A | Otonga |  | Hikurangi CB1032 | 2025-07-22 09:01 | 45860.3757 | 2025-07-22 14:13 | 45860.5924 | 0.59379 | 0.0019032 | 124 | 38688 | Planned | Planned Interruption | Replace crossarms, pole hardaware and refurbish transformers
|  | O-19741-A | North River |  | Ruakaka CB7 | 2025-07-22 12:41 | 45860.5285 | 2025-07-22 14:04 | 45860.5861 | 0.049682 | 0.00059858 | 39 | 3237 | Planned | Planned Interruption | Install new Tx RB341
|  | O-19270-A | Whatatiri |  | Maungatapere CB8 | 2025-07-23 09:04 | 45861.3778 | 2025-07-23 14:38 | 45861.6096 | 0.68642 | 0.0020567 | 134 | 44723 | Planned | Planned Interruption | Replace Poles and Hardware at various sites
|  | F-10351-A | Tangaihi |  | Ruawai CB1032 | 2025-07-23 11:27 | 45861.4773 | 2025-07-23 11:43 | 45861.4883 | 0.044556 | 0.0047733 | 311 | 2903 | Unplanned | Unknown | Close >15min. FPIs A,B,C & E SW 2059.
|  | F-10366-A | Turiwiri |  | Dargaville CB9 | 2025-07-23 19:09 | 45861.7979 | 2025-07-23 19:59 | 45861.8326 | 0.035301 | 0.00070602 | 46 | 2300 | Unplanned | Defective Equipment | 395095/ Faulty Ampact connection pole 22337
|  | O-19711-A | Coast |  | Dargaville CB6 | 2025-07-24 08:32 | 45862.3556 | 2025-07-24 15:28 | 45862.6447 | 1.0925 | 0.0026246 | 171 | 71179 | Planned | Planned Interruption | Install new transformer and Pole changes
|  | F-10369-A | Waipu |  | Ruakaka CB2 | 2025-07-24 15:30 | 45862.6458 | 2025-07-24 15:50 | 45862.6597 | 0.00061393 | 3.0697e-05 | 2 | 40 | Unplanned | Other Cause | FP395104 Tap change
|  | F-10372-A | North River |  | Ruakaka CB7 | 2025-07-24 21:32 | 45862.8972 | 2025-07-24 22:36 | 45862.9417 | 0.010805 | 0.00016883 | 11 | 704 | Unplanned | Defective Equipment | FP 395145 - Replace fauly DDOs, Corroded jumpers
|  | F-10375-A | Access Rd |  | Ruawai CB1022 | 2025-07-24 23:35 | 45862.9828 | 2025-07-24 23:51 | 45862.9934 | 0.054686 | 0.005111 | 333 | 3563 | Unplanned | Defective Equipment | B ph OC. No FPIs. Close >15 min. Broken binder found on F-10384-A
|  | O-19675-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-07-25 09:01 | 45863.3757 | 2025-07-25 12:15 | 45863.5104 | 0.059551 | 0.00030697 | 20 | 3880 | Planned | Planned Interruption | Replace HV Links Linked with O-19564-A outage (NAR 8895 & 8871)
|  | F-10378-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-07-25 11:30 | 45863.4791 | 2025-07-25 14:34 | 45863.6069 | 0.17885 | 0.0022408 | 146 | 11653 | Unplanned | Defective Equipment | FP 395166 Broken binder at pole 33316
|  | F-10384-A | Access Rd |  | Ruawai CB1022 | 2025-07-25 12:15 | 45863.5102 | 2025-07-25 17:02 | 45863.7097 | 0.19124 | 0.010114 | 659 | 12460 | Unplanned | Defective Equipment | FP395171 Broken binder causing line down btwn pole 39999 & pole 44208
|  | F-10390-A | Taipuha |  | Mareretu CB1 | 2025-07-25 15:02 | 45863.6262 | 2025-07-25 21:38 | 45863.9012 | 0.54098 | 0.001366 | 89 | 35247 | Unplanned | Defective Equipment | FP 395175 - HV line down, did not trip protection.
|  | F-10396-A | KAI - MTO POS |  | Maungaturoto POS CB1222 | 2025-07-27 00:13 | 45865.0092 | 2025-07-27 00:40 | 45865.0277 | 2.5366 | 0.1051 | 6848 | 165271 | Unplanned | Unknown | 33kV tripped O/C A&B ph indicating betwn MTO & MTON. Closed 33kV & 11kV in sections after 15mins. Daylight patrol FP395189
|  | O-19630-A | Kaka St |  | Whangarei South CB1032 | 2025-07-27 06:21 | 45865.2646 | 2025-07-27 18:19 | 45865.7632 | 0.0042361 | 0.00036836 | 24 | 276 | Planned | Planned Interruption | Installation of new safekink SW and TX
|  | O-19570-A | Jordan Valley |  | Hikurangi CB1102 | 2025-07-28 09:33 | 45866.3979 | 2025-07-28 12:31 | 45866.5215 | 0.11201 | 0.00062928 | 41 | 7298 | Planned | Planned Interruption | Tree Clearing Work
|  | O-19342-A | Kiripaka Rd |  | Tikipunga CB8 | 2025-07-28 09:44 | 45866.4056 | 2025-07-28 11:14 | 45866.4681 | 0.058016 | 0.00064463 | 42 | 3780 | Planned | Planned Interruption | Replace pillar at 6/8 Hawea Place
|  | F-10411-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-28 15:50 | 45866.6599 | 2025-07-28 16:06 | 45866.6709 | 0.16413 | 0.010345 | 674 | 10694 | Unplanned | Adverse Weather | Trip OC ABC, FPI's 349476, part of feeder could not restore prior due to tele Switch 302 Fail Sw 4228 was open at the time.
|  | F-10417-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-28 18:06 | 45866.754 | 2025-07-28 21:53 | 45866.9118 | 0.26288 | 0.014443 | 941 | 17128 | Unplanned | Defective Equipment | FP 395242 - broken binder pole 56361 (abnormal fdr config SW 4228 open, SW6202 clsoed)
|  | F-10426-A | North Kaiwaka |  | Kaiwaka CB1022 | 2025-07-28 22:49 | 45866.9507 | 2025-07-29 01:12 | 45867.05 | 0.19548 | 0.003392 | 221 | 12736 | Unplanned | Adverse Weather | FP 395245 - Switched and patrolled. Fault seen and heard between CB - Sw 10085 & Sw 313. Fault no longer apparent. Follow up req
|  | F-10429-A | North Dargaville |  | Dargaville CB1 | 2025-07-28 23:32 | 45866.9806 | 2025-07-29 04:49 | 45867.2007 | 0.27234 | 0.0046659 | 304 | 17744 | Unplanned | Defective Equipment | FP 395247 - Binder broken pole 24869
|  | F-10432-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-29 01:43 | 45867.0718 | 2025-07-29 02:16 | 45867.0943 | 0.30228 | 0.01036 | 675 | 19695 | Unplanned | Adverse Weather | Remotely livened in sections (excludes Sw 4228 - faulty, stuck open)
|  | F-10423-A | KAI - MTO POS |  | Maungaturoto POS CB1222 | 2025-07-29 02:32 | 45867.1052 | 2025-07-29 06:29 | 45867.2701 | 16.0099 | 0.073687 | 4801 | 1043108 | Unplanned | Defective Equipment | FP395245 - Emergency shut - rusty broken eye bolt (he held on by jumper). All 3 replaced. Loss of comms to MWN-locally restored
|  | F-10435-A | Swamp North |  | Hikurangi CB1042 | 2025-07-29 06:28 | 45867.2698 | 2025-07-29 12:08 | 45867.5056 | 0.37028 | 0.010099 | 658 | 24125 | Unplanned | Vegetation | FP 395252 - Clear tree & repair HV conductor
|  | F-10438-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-29 06:37 | 45867.2754 | 2025-07-29 06:58 | 45867.2902 | 0.20168 | 0.01036 | 675 | 13140 | Unplanned | Adverse Weather | AB O.C. White & Blue Ph FPIs from temp FPI 349476. Close <15min
|  | F-10441-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-29 08:11 | 45867.3411 | 2025-07-29 11:53 | 45867.4951 | 0.40868 | 0.02072 | 1350 | 26627 | Unplanned | Defective Equipment | FP 395258 - Resag 11kV line & ABC
|  | F-10447-A | Montgomery Ave |  | Onerahi CB8 | 2025-07-29 10:14 | 45867.4264 | 2025-07-29 13:47 | 45867.5743 | 0.10461 | 0.00049114 | 32 | 6816 | Unplanned | Defective Equipment | FP 395250 - Resag 11kV line
|  | F-10450-A | Tangowahine |  | Dargaville CB8 | 2025-07-29 13:09 | 45867.5479 | 2025-07-29 13:51 | 45867.5771 | 0.019339 | 0.00046045 | 30 | 1260 | Unplanned | Defective Equipment | FP 395265 - Replace arm brace bolt
|  | F-10453-A | Jordan Valley |  | Hikurangi CB1102 | 2025-07-29 16:19 | 45867.6797 | 2025-07-29 16:34 | 45867.6902 | 0.11017 | 0.0073365 | 478 | 7178 | Unplanned | Adverse Weather | ABC O.C. No FPIs. Close >15 min
|  | F-10462-A | Waipu |  | Ruakaka CB2 | 2025-07-29 19:00 | 45867.7916 | 2025-07-29 19:17 | 45867.8033 | 0.10326 | 0.015225 | 992 | 6728 | Unplanned | Adverse Weather | Sw 5434 indicating - livened remotely
|  | F-10456-A | Kensington |  | Alexander St CB8 | 2025-07-29 21:26 | 45867.8931 | 2025-07-29 23:19 | 45867.9715 | 0.21506 | 0.0019032 | 124 | 14012 | Unplanned | Defective Equipment | FP 395290 Cable term lug corroded, LA replaced.
|  | F-10471-A | Otonga |  | Hikurangi CB1032 | 2025-07-30 06:55 | 45868.2884 | 2025-07-30 13:50 | 45868.5764 | 1.0601 | 0.0091629 | 597 | 69069 | Unplanned | Vegetation | FP 395316 - Thick vegetation near lines, tree bought lines down.
|  | O-19450-A | Maungakaramea |  | Maungatapere CB3 | 2025-07-30 09:01 | 45868.3758 | 2025-07-30 12:06 | 45868.5044 | 0.47491 | 0.0025632 | 167 | 30942 | Planned | Planned Interruption | Replace HV and LV pole hardware at various sites
|  | O-19510-A | Bickerstaff |  | Maungaturoto CB2 | 2025-07-30 09:13 | 45868.384 | 2025-07-30 15:26 | 45868.6431 | 0.13167 | 0.00035301 | 23 | 8579 | Planned | Planned Interruption | Replace pole hardware at various sites
|  | O-19609-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-07-30 09:34 | 45868.3986 | 2025-07-30 12:50 | 45868.5347 | 0.12334 | 0.00062928 | 41 | 8036 | Planned | Planned Interruption | Tree Clearing Work
|  | F-10483-A | Jordan Valley |  | Hikurangi CB1102 | 2025-07-30 17:45 | 45868.7396 | 2025-07-30 17:46 | 45868.7405 | 0.0092857 | 0.0073365 | 478 | 605 | Unplanned | Unknown | Trip & Close (F5) - Trip O/C ABC
|  | O-19750-A | Hakaru |  | Kaiwaka CB1032 | 2025-07-31 09:05 | 45869.3785 | 2025-07-31 15:23 | 45869.641 | 2.4889 | 0.0065844 | 429 | 162162 | Planned | Planned Interruption | Replace crossarm, hardware and connections
|  | F-274-B | Te Kopuru |  | Dargaville CB2 | 2025-07-31 13:21 | 45869.5563 | 2025-07-31 14:32 | 45869.6056 | 0.062114 | 0.00087485 | 57 | 4047 | Unplanned | Defective Equipment | 395358. Missing Xarm Brace
|  | F-10498-A | King Road |  | Mangawhai North CB2 | 2025-07-31 19:42 | 45869.8208 | 2025-07-31 22:09 | 45869.923 | 0.15766 | 0.0022101 | 144 | 10272 | Unplanned | Defective Equipment | 395376/ Jumper connection fault to top of HV Fuse
|  | O-19366-A | Otangarei |  | Tikipunga CB7 | 2025-08-01 09:05 | 45870.3785 | 2025-08-01 13:09 | 45870.5479 | 0.011204 | 4.6045e-05 | 3 | 730 | Planned | Planned Interruption | Replace RMU
|  | F-10510-A | Jordan Valley |  | Hikurangi CB1102 | 2025-08-03 18:53 | 45872.7866 | 2025-08-04 03:18 | 45873.1375 | 0.38045 | 0.0073365 | 478 | 24788 | Unplanned | Third Party Interference | 395424 Car Vs pole 35090 (event # F4264805) Note: Fdr was in abnormal config at time of tripping.
|  | F-10513-A | Marsden South |  | Bream Bay CB1111 | 2025-08-04 06:57 | 45873.2895 | 2025-08-04 07:11 | 45873.2995 | 0.022577 | 0.0015655 | 102 | 1471 | Unplanned | Unknown | B Ph OC. No FPIs.
|  | O-6808-B | Town Dargaville |  | Dargaville CB3 | 2025-08-05 22:52 | 45874.9528 | 2025-08-06 03:10 | 45875.1319 | 0.059398 | 0.00023022 | 15 | 3870 | Planned | Planned Interruption | Replacing HV bushings
|  | O-20074-A | Tangaihi |  | Ruawai CB1032 | 2025-08-06 09:05 | 45875.3785 | 2025-08-06 13:48 | 45875.575 | 0.021718 | 7.6741e-05 | 5 | 1415 | Planned | Planned Interruption | Install new transformer and replace poles and hardware
|  | O-19411-A | Beach Road |  | Onerahi CB2 | 2025-08-07 09:01 | 45876.3757 | 2025-08-07 14:27 | 45876.6021 | 1.411 | 0.0043282 | 282 | 91932 | Planned | Planned Interruption | Replace HV/LV poles and hardware
|  | O-20092-A | Wairere |  | Mareretu CB5 | 2025-08-07 09:04 | 45876.3779 | 2025-08-07 17:51 | 45876.7438 | 0.26683 | 0.00050649 | 33 | 17385 | Planned | Planned Interruption | Replace cross-arms and re-terminate cable
|  | F-10531-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-08-07 16:49 | 45876.7008 | 2025-08-07 17:04 | 45876.7113 | 0.050634 | 0.0078276 | 510 | 3299 | Unplanned | Unknown | Trip A & B Phase Overcurrent. Fault past Sw 320. 15 min close on Sw 320 & BTN.
|  | O-19621-A | Town Dargaville |  | Dargaville CB3 | 2025-08-07 23:21 | 45876.9729 | 2025-08-08 02:35 | 45877.1076 | 0.017865 | 9.209e-05 | 6 | 1164 | Planned | Planned Interruption | Repair LV bushing oil leak and test earth mat
|  | O-19903-A | Bickerstaff |  | Maungaturoto CB2 | 2025-08-08 09:01 | 45877.3758 | 2025-08-08 12:09 | 45877.5065 | 0.24266 | 0.0012893 | 84 | 15810 | Planned | Planned Interruption | Re-sag HV/LV lines
|  | O-19321-A | Tamaterau |  | Onerahi CB7 | 2025-08-08 09:02 | 45877.3766 | 2025-08-08 12:29 | 45877.52 | 0.37728 | 0.0018264 | 119 | 24581 | Planned | Planned Interruption | Replace pole & hardware
|  | F-10534-A | North Dargaville |  | Dargaville CB1 | 2025-08-08 22:07 | 45877.9216 | 2025-08-08 22:24 | 45877.9333 | 0.039077 | 0.0023329 | 152 | 2546 | Unplanned | Unknown | Trip O/C Phase AB
|  | F-10537-A | Mata |  | Ruakaka CB3 | 2025-08-09 11:11 | 45878.4662 | 2025-08-09 15:01 | 45878.6257 | 0.5177 | 0.028011 | 1825 | 33730 | Unplanned | Defective Equipment | 395611 Found floating HV wire (Broken binder) at pole 47076
|  | F-10540-A | Te Hihi |  | Maunu CB1022 | 2025-08-09 11:49 | 45878.4924 | 2025-08-09 20:59 | 45878.8742 | 1.1433 | 0.0096541 | 629 | 74493 | Unplanned | Third Party Interference | FP395608 Car VS pole @ pole 328937 (Event number F-4268186)
|  | F-10543-A | Te Kopuru |  | Dargaville CB2 | 2025-08-09 14:35 | 45878.6076 | 2025-08-09 15:20 | 45878.6389 | 0.012432 | 0.00027627 | 18 | 810 | Unplanned | Defective Equipment | 395610 Replace broken DDO's at Tx L203
|  | F-10546-A | Whakapara |  | Hikurangi CB1112 | 2025-08-09 21:58 | 45878.9153 | 2025-08-10 07:55 | 45879.3297 | 1.514 | 0.016684 | 1087 | 98642 | Unplanned | Third Party Interference | 395617 Car Vs pole @ pole 42017 - (Very Busy Pole)
|  | O-19930-A | Three Mile Bush |  | Kamo CB3 | 2025-08-10 09:04 | 45879.3778 | 2025-08-10 15:39 | 45879.6521 | 0.27282 | 0.00069067 | 45 | 17775 | Planned | Planned Interruption | Upgrade Tx KK115 and pole hardware
|  | F-10555-A | Kokopu |  | Poroti CB1022 | 2025-08-11 10:46 | 45880.4485 | 2025-08-11 11:26 | 45880.4767 | 0.19795 | 0.0062774 | 409 | 12897 | Unplanned | Wildlife | 395647 Relivened in sections - Report of possum on lines - checked & cleared from LV P485
|  | F-10561-A | Swamp North |  | Hikurangi CB1042 | 2025-08-11 22:20 | 45880.9308 | 2025-08-11 22:35 | 45880.9413 | 0.093456 | 0.006216 | 405 | 6089 | Unplanned | Unknown | O/C B&C phase - No FPIs activated - Unknown
|  | O-19453-A | Whatatiri |  | Maungatapere CB8 | 2025-08-12 08:27 | 45881.3521 | 2025-08-12 13:21 | 45881.5563 | 0.7127 | 0.0028394 | 185 | 46435 | Planned | Planned Interruption | Replace poles for height mitigation
|  | F-10564-A | Three Mile Bush |  | Kamo CB3 | 2025-08-12 19:19 | 45881.8049 | 2025-08-13 05:16 | 45882.2194 | 1.0171 | 0.0017037 | 111 | 66267 | Unplanned | Third Party Interference | 395714 Car Vs pole @ pole 52686
|  | O-19963-A | Pataua |  | Parua Bay CB1 | 2025-08-13 09:04 | 45882.3775 | 2025-08-13 14:59 | 45882.6244 | 1.0808 | 0.003039 | 198 | 70419 | Planned | Planned Interruption | Replace pole #43031 and upgrade Tx OO465 to 100kVA
|  | O-19108-A | Otonga |  | Hikurangi CB1032 | 2025-08-13 09:04 | 45882.3778 | 2025-08-13 14:21 | 45882.5979 | 1.2212 | 0.0038524 | 251 | 79567 | Planned | Planned Interruption | Replace poles, cross-arms and refurbish various Dsubs
|  | O-6742-B | Tangaihi |  | Ruawai CB1032 | 2025-08-13 09:37 | 45882.4007 | 2025-08-13 14:18 | 45882.5958 | 0.021564 | 7.6741e-05 | 5 | 1405 | Planned | Planned Interruption | HV isolation for LV works
|  | O-6817-B | Montgomery Ave |  | Onerahi CB8 | 2025-08-14 09:06 | 45883.3792 | 2025-08-14 14:12 | 45883.5917 | 0.0046966 | 1.5348e-05 | 1 | 306 | Planned | Planned Interruption | Upgrade Tx OP229
|  | O-6736-B | Langs Beach |  | Mangawhai North CB3 | 2025-08-14 09:14 | 45883.3847 | 2025-08-14 19:20 | 45883.8056 | 0.35105 | 0.00058323 | 38 | 22872 | Planned | Planned Interruption | Remove RMU, Install 2x RMU's. Additional restoration switching to ensure Phase Rotation checks ok on several Tx's.
|  | O-20008-A | Tangaihi |  | Ruawai CB1032 | 2025-08-14 09:39 | 45883.4021 | 2025-08-14 12:40 | 45883.5278 | 0.02778 | 0.00015348 | 10 | 1810 | Planned | Planned Interruption | Tree Clearing Work
|  | F-10588-A | Dunns Rd |  | Ruawai CB1082 | 2025-08-15 10:09 | 45884.423 | 2025-08-15 11:09 | 45884.4647 | 0.023038 | 0.00038371 | 25 | 1501 | Unplanned | Defective Equipment | 395776 / Isolate HV to replace bolt on X Arm at pole 44922
|  | F-283-B | Marsden Bay |  | Bream Bay CB1107 | 2025-08-15 16:15 | 45884.6771 | 2025-08-15 18:36 | 45884.775 | 0.0043282 | 3.0697e-05 | 2 | 282 | Unplanned | Defective Equipment | To repair oil leak at Tx
|  | F-10594-A | Otonga |  | Hikurangi CB1032 | 2025-08-16 04:14 | 45885.1766 | 2025-08-16 13:19 | 45885.5549 | 1.0999 | 0.025923 | 1689 | 71665 | Unplanned | Wildlife | Took a long time to find fault in among trees ETC. HV Lines down found at pole 58339. Unknown Cause. BTN FP395812
|  | F-10603-A | Marua |  | Hikurangi CB1022 | 2025-08-16 20:09 | 45885.8393 | 2025-08-16 22:09 | 45885.9229 | 0.91178 | 0.056512 | 3682 | 59406 | Unplanned | Defective Equipment | Fault in crutch of cable at crucifix CP30 Whakapara tripped whilst paralleling OC tripping at 100A instead of 200A FP395821
|  | F-10606-A | North River |  | Ruakaka CB7 | 2025-08-16 21:38 | 45885.9016 | 2025-08-17 01:12 | 45886.05 | 0.016392 | 7.6741e-05 | 5 | 1068 | Unplanned | Defective Equipment | Jumper off line side of Fuses RB186 - replaced 2 x HV fuse bases FP 395820
|  | F-10609-A | Whatatiri |  | Maungatapere CB8 | 2025-08-17 04:39 | 45886.1938 | 2025-08-17 09:34 | 45886.3989 | 1.2856 | 0.028655 | 1867 | 83760 | Unplanned | Defective Equipment | FP395823 Floating HV jumper off on line side of HV fuses Tx WC483
|  | O-19942-A | Walton St |  | Whangarei South CB1022 | 2025-08-17 08:08 | 45886.3389 | 2025-08-17 15:13 | 45886.634 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Install and liven new switch 10265, 10264, 10263
|  | O-19552-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-18 09:07 | 45887.3799 | 2025-08-18 13:20 | 45887.5556 | 0.0038831 | 1.5348e-05 | 1 | 253 | Planned | Planned Interruption | Replace Poles and hardware
|  | O-19864-A | ToeToe Rd |  | Kioreroa CB7 | 2025-08-18 10:07 | 45887.4215 | 2025-08-18 14:32 | 45887.6056 | 0.040673 | 0.00015348 | 10 | 2650 | Planned | Planned Interruption | Relocate transformer and decommsion 11kV line
|  | F-10624-A | Paranui |  | Tikipunga CB6 | 2025-08-18 12:53 | 45887.5369 | 2025-08-18 19:35 | 45887.816 | 0.70912 | 0.018065 | 1177 | 46202 | Unplanned | Vegetation | 395856 / HV Lines down Pole 51443.
|  | O-7033-B | Fert. Works |  | Kioreroa CB6 | 2025-08-18 15:08 | 45887.6306 | 2025-08-18 19:00 | 45887.7917 | 0.0071216 | 3.0697e-05 | 2 | 464 | Planned | Planned Interruption | Replace bushings and gasket
|  | F-10636-A | Tangaihi |  | Ruawai CB1032 | 2025-08-19 05:58 | 45888.2483 | 2025-08-19 08:28 | 45888.3528 | 0.0092396 | 6.1393e-05 | 4 | 602 | Unplanned | Lightning | 395872/ x3 Blown HV Fuses
|  | O-19558-A | Swamp North |  | Hikurangi CB1042 | 2025-08-19 09:14 | 45888.3847 | 2025-08-19 15:17 | 45888.6368 | 0.93043 | 0.0025632 | 167 | 60621 | Planned | Planned Interruption | Replace HV/LV crossarms and refurbish Dsub KB 150
|  | O-6805-B | Maunu Mountain |  | Maungatapere CB1 | 2025-08-19 09:30 | 45888.3958 | 2025-08-19 14:04 | 45888.5861 | 0.91258 | 0.0033306 | 217 | 59458 | Planned | Planned Interruption | Pole changes to increase road crossing heights
|  | O-20038-A | Whatatiri |  | Maungatapere CB8 | 2025-08-19 09:52 | 45888.4114 | 2025-08-19 14:58 | 45888.6234 | 0.47306 | 0.0015502 | 101 | 30822 | Planned | Planned Interruption | Tree Clearing Work
|  | O-6871-B | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-08-20 09:04 | 45889.3778 | 2025-08-20 14:11 | 45889.591 | 0.037695 | 0.00012279 | 8 | 2456 | Planned | Planned Interruption | Replace Poles and install new transformers
|  | O-19567-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-20 09:06 | 45889.3792 | 2025-08-20 13:56 | 45889.5806 | 0.035608 | 0.00012279 | 8 | 2320 | Planned | Planned Interruption | Refurbish transformer and replace pole hardware
|  | F-10669-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-20 12:36 | 45889.5251 | 2025-08-20 13:06 | 45889.546 | 0.057218 | 0.0019032 | 124 | 3728 | Unplanned | Human Error | A C phase O/C. Reclose Block to straighten pole returned and cancelled. Ensured safe to reliven then proceeded with restoration.
|  | F-10672-A | Te Kopuru |  | Dargaville CB2 | 2025-08-20 15:18 | 45889.6375 | 2025-08-20 19:06 | 45889.7958 | 0.062989 | 0.00027627 | 18 | 4104 | Unplanned | Defective Equipment | 395936 Replace burnt out HV Xarm, jumpers & HV fuses K183
|  | F-10681-A | Parua Bay |  | Parua Bay CB2 | 2025-08-21 02:53 | 45890.12 | 2025-08-21 03:08 | 45890.1304 | 0.13637 | 0.0090708 | 591 | 8885 | Unplanned | Unknown | Tripped O/C A&B phase, Unknown cause
|  | O-6895-B | Coast |  | Dargaville CB6 | 2025-08-21 08:44 | 45890.3639 | 2025-08-21 17:38 | 45890.7347 | 0.12294 | 0.00023022 | 15 | 8010 | Planned | Planned Interruption | Re-sag 11kV Line
|  | O-19837-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-21 09:08 | 45890.3806 | 2025-08-21 13:40 | 45890.5694 | 0.23796 | 0.00087485 | 57 | 15504 | Planned | Planned Interruption | Replace HV and LV poles crossarms and connections
|  | F-10693-A | Bickerstaff |  | Maungaturoto CB2 | 2025-08-21 22:56 | 45890.9559 | 2025-08-21 23:19 | 45890.9716 | 0.23431 | 0.010345 | 674 | 15266 | Unplanned | Defective Equipment | Trip EF - O/C Bphase - Found later to be HV lines down. see FP395972
|  | O-7111-B | Union East |  | Kioreroa CB1 | 2025-08-22 01:03 | 45891.0437 | 2025-08-22 03:50 | 45891.1597 | 0.0051263 | 3.0697e-05 | 2 | 334 | Planned | Planned Interruption | Carry out LV works. Isolation for customer Switchboard works
|  | F-10696-A | Bickerstaff |  | Maungaturoto CB2 | 2025-08-22 05:41 | 45891.237 | 2025-08-22 09:22 | 45891.39 | 0.82988 | 0.01036 | 675 | 54070 | Unplanned | Defective Equipment | 395972/ De-energised for safety, lines down across road & cable smoking. Large outage area due to failed to operate tele switch.
|  | O-20002-A | Beach Road |  | Onerahi CB2 | 2025-08-22 09:10 | 45891.3819 | 2025-08-22 14:10 | 45891.5903 | 0.096694 | 0.00032231 | 21 | 6300 | Planned | Planned Interruption | Replace LV arms and hardware
|  | O-6826-B | Bickerstaff |  | Maungaturoto CB2 | 2025-08-22 10:21 | 45891.4312 | 2025-08-22 14:00 | 45891.5833 | 0.14799 | 0.00067532 | 44 | 9642 | Planned | Planned Interruption | Re-sag HV and LV line - Delay to outage start time due to feeder fault using traffic management nearby
|  | F-10675-A | North Dargaville |  | Dargaville CB1 | 2025-08-22 11:31 | 45891.4799 | 2025-08-22 13:59 | 45891.5826 | 0.040888 | 0.00027627 | 18 | 2664 | Unplanned | Defective Equipment | FP 395978 - Replace King bolt & Nut on HV insulator
|  | O-20029-A | Tangowahine |  | Dargaville CB8 | 2025-08-25 10:07 | 45894.4215 | 2025-08-25 15:11 | 45894.6326 | 0.11665 | 0.00038371 | 25 | 7600 | Planned | Planned Interruption | Replace HV/LV crossarms
|  | O-6814-B | Coast |  | Dargaville CB6 | 2025-08-26 08:46 | 45895.3651 | 2025-08-26 17:20 | 45895.7222 | 0.83651 | 0.0016269 | 106 | 54502 | Planned | Planned Interruption | Repalce and Install Pole Due to work load went over advertised time by 50mins
|  | O-19663-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-26 09:11 | 45895.3826 | 2025-08-26 13:09 | 45895.5479 | 0.036529 | 0.00015348 | 10 | 2380 | Planned | Planned Interruption | Replace pole hardware
|  | O-6796-B | Coast |  | Dargaville CB6 | 2025-08-26 09:33 | 45895.3977 | 2025-08-26 11:29 | 45895.4788 | 0.5537 | 0.0047426 | 309 | 36076 | Planned | Planned Interruption | Replace lightning arrestors for Tx L116
|  | F-10744-A | Paranui |  | Tikipunga CB6 | 2025-08-26 11:10 | 45895.4651 | 2025-08-26 11:56 | 45895.4973 | 0.23406 | 0.011373 | 741 | 15250 | Unplanned | Unknown | 396069 O/C A&B phase, FPI's activated at Sw 7022, Customer advised noise, patrolled and nothing found.
|  | F-10747-A | Titoki |  | Poroti CB1032 | 2025-08-26 21:29 | 45895.8951 | 2025-08-27 00:01 | 45896.0007 | 0.35175 | 0.0073979 | 482 | 22918 | Unplanned | Unknown | 396096 / Trip A B & C. Closed in section by section from Sw 831 & Held. BTN
|  | O-19993-A | Maungakaramea |  | Maungatapere CB3 | 2025-08-27 08:29 | 45896.3535 | 2025-08-27 15:32 | 45896.6472 | 0.96887 | 0.0026092 | 170 | 63126 | Planned | Planned Interruption | Replace poles, crossarms, transformers and connections
|  | O-6886-B | Coast |  | Dargaville CB6 | 2025-08-27 08:34 | 45896.3569 | 2025-08-27 16:02 | 45896.6683 | 0.19957 | 0.0004451 | 29 | 13003 | Planned | Planned Interruption | Resag existing conductor
|  | O-6898-B | Thelma Road |  | Mangawhai North CB4 | 2025-08-27 09:16 | 45896.3861 | 2025-08-27 16:52 | 45896.7028 | 0.45492 | 0.00099764 | 65 | 29640 | Planned | Planned Interruption | Relocate RMU
|  | F-10753-A | Charles St |  | Kamo CB2 | 2025-08-27 11:26 | 45896.4764 | 2025-08-27 12:47 | 45896.5326 | 0.080809 | 0.00099764 | 65 | 5265 | Unplanned | Third Party Interference | FP 396100 - shutdown to reposition Tx KT365 after vehicle damage
|  | O-19354-A | Ararua |  | Mareretu CB2 | 2025-08-28 09:04 | 45897.3778 | 2025-08-28 13:06 | 45897.5458 | 0.070571 | 0.00029162 | 19 | 4598 | Planned | Planned Interruption | Replace poles, crossarms and straighten poles
|  | F-10759-A | Coast |  | Dargaville CB6 | 2025-08-28 11:32 | 45897.4806 | 2025-08-28 13:42 | 45897.5708 | 0.025939 | 0.00019953 | 13 | 1690 | Unplanned | Defective Equipment | FP 396144 - Replace insulators after report of floating 11kV
|  | O-6943-B | Coast |  | Dargaville CB6 | 2025-08-29 08:57 | 45898.373 | 2025-08-29 14:49 | 45898.6175 | 0.23773 | 0.00067532 | 44 | 15489 | Planned | Planned Interruption | 66kV conductor works
|  | F-10771-A | Swamp South |  | Hikurangi CB1092 | 2025-08-30 06:37 | 45899.2758 | 2025-08-30 06:53 | 45899.287 | 0.0052338 | 0.00032231 | 21 | 341 | Unplanned | Unknown | Remote Sw 6144 indicating B&C. No comms. Entire feeder closed in 15min
|  | F-10774-A | Whakapara |  | Hikurangi CB1112 | 2025-08-30 11:50 | 45899.4933 | 2025-08-30 17:09 | 45899.7146 | 1.2934 | 0.016745 | 1091 | 84273 | Unplanned | Vegetation | Lines down due to tree felled thru. (unidentified tree feller) FP 396220
|  | F-10804-A | Mata |  | Ruakaka CB3 | 2025-08-31 16:05 | 45900.6701 | 2025-08-31 16:40 | 45900.6945 | 0.12187 | 0.00683 | 445 | 7940 | Unplanned | Third Party Interference | Trip a b & c Overcurrent. Reported trampoline clashed with lines causing LV lines down. Livened BTN
|  | F-10807-A | Otonga |  | Hikurangi CB1032 | 2025-08-31 16:41 | 45900.6949 | 2025-08-31 16:56 | 45900.7053 | 0.13614 | 0.0091169 | 594 | 8870 | Unplanned | Adverse Weather | Trip & 15 Min Close. BTN
|  | F-10813-A | Onoke |  | Kamo CB8 | 2025-08-31 18:04 | 45900.7529 | 2025-08-31 20:28 | 45900.8528 | 0.098306 | 0.001366 | 89 | 6405 | Unplanned | Defective Equipment | Replaced faulty HV Fuse base - FP369247
|  | F-10804-A | Mata |  | Ruakaka CB3 | 2025-08-31 18:43 | 45900.7799 | 2025-08-31 19:38 | 45900.8181 | 0.058247 | 0.001059 | 69 | 3795 | Unplanned | Third Party Interference | Repaired spragged 11KV, repaired LV lines down and tested for Hi LO clash. due to trampoline hitting lines FP396244
|  | F-10822-A | Coast |  | Dargaville CB6 | 2025-08-31 20:49 | 45900.8675 | 2025-08-31 23:53 | 45900.9953 | 0.8824 | 0.027965 | 1822 | 57492 | Unplanned | Defective Equipment | FP 396270 - Rebind centre phase back in
|  | F-10825-A | Te Kopuru |  | Dargaville CB2 | 2025-09-01 00:48 | 45901.0333 | 2025-09-01 05:45 | 45901.2396 | 0.23438 | 0.0039598 | 258 | 15271 | Unplanned | Defective Equipment | FP 396273 - Replace burnt crossarm
|  | O-7099-B | Hokianga Rd |  | Dargaville CB7 | 2025-09-01 09:02 | 45901.3764 | 2025-09-01 17:57 | 45901.7479 | 0.049268 | 9.209e-05 | 6 | 3210 | Planned | Planned Interruption | Installing new 66kV conductor works
|  | O-6985-B | Taipuha |  | Mareretu CB1 | 2025-09-01 09:21 | 45901.3896 | 2025-09-01 13:43 | 45901.5715 | 0.23725 | 0.00090555 | 59 | 15458 | Planned | Planned Interruption | Pole replacement
|  | O-7048-B | Mangawhai Heads |  | Mangawhai North CB1 | 2025-09-01 09:37 | 45901.4007 | 2025-09-01 11:40 | 45901.4861 | 0.51601 | 0.0042822 | 279 | 33620 | Planned | Planned Interruption | Liven new RMU and Tx MC585
|  | F-10834-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-09-01 11:55 | 45901.4965 | 2025-09-01 17:09 | 45901.7146 | 0.55416 | 0.0021334 | 139 | 36106 | Unplanned | Third Party Interference | FP 396274 - Car Vs Pole
|  | F-10840-A | Jordan Valley |  | Hikurangi CB1102 | 2025-09-01 13:15 | 45901.5521 | 2025-09-01 18:03 | 45901.7519 | 0.013414 | 7.6741e-05 | 5 | 874 | Unplanned | Defective Equipment | Replaced HV fuse bases FP396295
|  | O-6904-B | Kokopu |  | Poroti CB1022 | 2025-09-02 09:11 | 45902.3826 | 2025-09-02 13:02 | 45902.5431 | 0.078 | 0.00033766 | 22 | 5082 | Planned | Planned Interruption | Level Tx P439
|  | O-6997-B | Paparoa |  | Mareretu CB6 | 2025-09-03 09:05 | 45903.3785 | 2025-09-03 13:31 | 45903.5632 | 0.048992 | 0.00018418 | 12 | 3192 | Planned | Planned Interruption | Replacing crossarms
|  | O-6790-B | Tamaterau |  | Onerahi CB7 | 2025-09-03 09:07 | 45903.3799 | 2025-09-03 13:19 | 45903.5549 | 0.35583 | 0.001412 | 92 | 23184 | Planned | Planned Interruption | Crossarm and hardware & Pole replacements
|  | O-6952-B | Taipuha |  | Mareretu CB1 | 2025-09-03 09:38 | 45903.4014 | 2025-09-03 15:01 | 45903.6257 | 0.1983 | 0.00061393 | 40 | 12920 | Planned | Planned Interruption | Repalcing crossarms, pole and DOF's
|  | O-7108-B | Marsden Bay |  | Bream Bay CB1107 | 2025-09-04 09:20 | 45904.3889 | 2025-09-04 14:28 | 45904.6028 | 0.16545 | 0.00053719 | 35 | 10780 | Planned | Planned Interruption | Repalce Tx RO271
|  | O-7000-B | Taipuha |  | Mareretu CB1 | 2025-09-04 10:04 | 45904.4195 | 2025-09-04 15:18 | 45904.6376 | 0.20243 | 0.00064463 | 42 | 13189 | Planned | Planned Interruption | Installang new poles
|  | F-10858-A | Paparoa |  | Mareretu CB6 | 2025-09-05 02:55 | 45905.1214 | 2025-09-05 03:11 | 45905.1324 | 0.14432 | 0.0090862 | 592 | 9403 | Unplanned | Unknown | Trip OC Phase AB
|  | O-6937-B | One Tree Point |  | Ruakaka CB6 | 2025-09-05 09:04 | 45905.3778 | 2025-09-05 14:29 | 45905.6035 | 0.1247 | 0.00038371 | 25 | 8125 | Planned | Planned Interruption | Re-route 11kV conductors
|  | O-6832-B | Bickerstaff |  | Maungaturoto CB2 | 2025-09-05 09:14 | 45905.3847 | 2025-09-05 15:07 | 45905.6299 | 0.33049 | 0.00093624 | 61 | 21533 | Planned | Planned Interruption | Repalce crossarms, Tx D161 and hardwares
|  | F-10861-A | Ararua |  | Mareretu CB2 | 2025-09-05 17:53 | 45905.745 | 2025-09-05 18:08 | 45905.7556 | 0.0039905 | 0.00026092 | 17 | 260 | Unplanned | Other Cause | FP396411 Isolate for Tap change
|  | F-10867-A | Taipuha |  | Mareretu CB1 | 2025-09-06 06:51 | 45906.2856 | 2025-09-06 10:06 | 45906.4208 | 0.090631 | 0.0011511 | 75 | 5905 | Unplanned | Defective Equipment | Replaced 3x Jumpers ( one blown off) Patrolled feeder OK FP396455
|  | F-10870-A | Marua |  | Hikurangi CB1022 | 2025-09-07 17:11 | 45907.716 | 2025-09-07 17:27 | 45907.7272 | 0.048946 | 0.0048654 | 317 | 3189 | Unplanned | Unknown | O/C B & C
|  | F-10873-A | Ararua |  | Mareretu CB2 | 2025-09-07 18:42 | 45907.7792 | 2025-09-07 18:58 | 45907.7903 | 0.16507 | 0.01036 | 675 | 10755 | Unplanned | Unknown | B&C Phase OC. 15 min close
|  | O-6838-B | Whau Valley |  | Tikipunga CB1 | 2025-09-09 08:33 | 45909.3562 | 2025-09-09 14:46 | 45909.6153 | 0.19465 | 0.00052184 | 34 | 12682 | Planned | Planned Interruption | Remove 11KV cable from SW 7057 and re direct to new SW10260
|  | F-10882-A | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-09-09 09:26 | 45909.3931 | 2025-09-09 10:19 | 45909.4299 | 0.051248 | 0.00096694 | 63 | 3339 | Unplanned | Vegetation | FP 396508 / Clear Bamboo. Suspected cause of RECL 1541 auto reclose recently.
|  | O-7132-B | Otonga |  | Hikurangi CB1032 | 2025-09-09 09:40 | 45909.4028 | 2025-09-09 14:50 | 45909.6181 | 0.39491 | 0.0012739 | 83 | 25730 | Planned | Planned Interruption | Redo connections and remove LA's
|  | F-10888-A | Kaiwaka South |  | Kaiwaka CB1072 | 2025-09-09 21:14 | 45909.8848 | 2025-09-09 21:30 | 45909.8956 | 0.054364 | 0.0078583 | 512 | 3542 | Unplanned | Unknown | T & C - FPIS Sw 320 activated A.B & C phase
|  | F-10891-A | Maungakaramea |  | Maungatapere CB3 | 2025-09-10 05:25 | 45910.2259 | 2025-09-10 05:40 | 45910.2364 | 0.11061 | 0.009255 | 603 | 7207 | Unplanned | Unknown | Report of a flash at end of Pukeatua Rd Tx X171
|  | O-6868-B | Langs Beach |  | Mangawhai North CB3 | 2025-09-10 09:02 | 45910.3765 | 2025-09-10 15:10 | 45910.6321 | 1.1244 | 0.0030543 | 199 | 73259 | Planned | Planned Interruption | Replace poles, hardware and the Tx
|  | O-6841-B | Three Mile Bush |  | Kamo CB3 | 2025-09-10 09:05 | 45910.3785 | 2025-09-10 12:44 | 45910.5306 | 0.12773 | 0.00058323 | 38 | 8322 | Planned | Planned Interruption | Joint 11KV cable from SW7056 to SW10261
|  | O-6925-B | Maunu Mountain |  | Maungatapere CB1 | 2025-09-11 09:01 | 45911.3754 | 2025-09-11 12:48 | 45911.5337 | 0.17494 | 0.00076741 | 50 | 11398 | Planned | Planned Interruption | Install new automated switch 10322 and remove SW 761
|  | O-7066-B | Tamaterau |  | Onerahi CB7 | 2025-09-11 09:02 | 45911.3764 | 2025-09-11 14:40 | 45911.6111 | 0.53952 | 0.0015962 | 104 | 35152 | Planned | Planned Interruption | HV/LV hardware replacement with spur line conductor
|  | O-7153-B | Bickerstaff |  | Maungaturoto CB2 | 2025-09-11 09:08 | 45911.3806 | 2025-09-11 13:29 | 45911.5618 | 0.030436 | 0.00012279 | 8 | 1983 | Planned | Planned Interruption | Replace pole and liven new Tx D454
|  | O-6877-B | Langs Beach |  | Mangawhai North CB3 | 2025-09-11 09:55 | 45911.4132 | 2025-09-11 11:39 | 45911.4854 | 0.081407 | 0.00078276 | 51 | 5304 | Planned | Planned Interruption | Replace Tx kennel
|  | F-10900-A | Te Kopuru |  | Dargaville CB2 | 2025-09-12 09:07 | 45912.3797 | 2025-09-12 14:04 | 45912.5861 | 0.55202 | 0.014596 | 951 | 35966 | Unplanned | Vegetation | FP 396610 - Cleared trees and repair broken HV lines
|  | O-7006-B | Paparoa |  | Mareretu CB6 | 2025-09-12 09:19 | 45912.3882 | 2025-09-12 13:54 | 45912.5792 | 0.15617 | 0.00056789 | 37 | 10175 | Planned | Planned Interruption | Replace x-arms and hardware
|  | F-10903-A | Ararua |  | Mareretu CB2 | 2025-09-12 11:10 | 45912.4651 | 2025-09-12 11:28 | 45912.478 | 0.042791 | 0.0023022 | 150 | 2788 | Unplanned | Adverse Weather | A,B & C OC. Close >15min
|  | F-10909-A | Dunns Rd |  | Ruawai CB1082 | 2025-09-12 16:00 | 45912.6668 | 2025-09-12 19:49 | 45912.8257 | 0.34781 | 0.0015195 | 99 | 22661 | Unplanned | Defective Equipment | 396602 2x faults found - Blown jumper at pole 22818 & Broken LA at Recl 1505
|  | F-10912-A | North Dargaville |  | Dargaville CB1 | 2025-09-12 17:09 | 45912.7146 | 2025-09-12 17:20 | 45912.7222 | 0.0013506 | 0.00012279 | 8 | 88 | Unplanned | Other Cause | FP396619 - removed solid links, fit 6A Fuses to 3002
|  | F-10924-A | Taipuha |  | Mareretu CB1 | 2025-09-14 11:02 | 45914.4594 | 2025-09-14 11:17 | 45914.4699 | 0.041225 | 0.0070755 | 461 | 2686 | Unplanned | Unknown | SW 364 FPI's activated A & B phase
|  | F-10930-A | Whatatiri |  | Maungatapere CB8 | 2025-09-15 06:04 | 45915.2525 | 2025-09-15 06:18 | 45915.2628 | 0.086748 | 0.0093778 | 611 | 5652 | Unplanned | Unknown | O/C B&C
|  | F-10939-A | Bickerstaff |  | Maungaturoto CB2 | 2025-09-16 06:29 | 45916.27 | 2025-09-16 06:46 | 45916.2817 | 0.15516 | 0.010283 | 670 | 10109 | Unplanned | Unknown | FPI 349476 indicating, livened in sections.
|  | O-7192-B | Maunu |  | Maunu CB1032 | 2025-09-16 09:19 | 45916.3882 | 2025-09-16 15:15 | 45916.6354 | 0.53162 | 0.0015348 | 100 | 34637 | Planned | Planned Interruption | Replace crossarms on LV poles
|  | F-10942-A | Langs Beach |  | Mangawhai North CB3 | 2025-09-16 23:09 | 45916.9647 | 2025-09-17 05:18 | 45917.221 | 1.3684 | 0.033613 | 2764 | 89663 | Unplanned | Defective Equipment | SW 10231 FPI E/F activated Repaired a jumper burning on the crossarm
|  | O-19678-A | Maungakaramea |  | Maungatapere CB3 | 2025-09-17 09:06 | 45917.3792 | 2025-09-17 16:00 | 45917.6667 | 0.48292 | 0.0011665 | 76 | 31464 | Planned | Planned Interruption | Repalcing Poles, crossarms and re-doing connections.
|  | O-7051-B | Marsden Pt |  | Ruakaka CB1 | 2025-09-18 09:04 | 45918.3778 | 2025-09-18 13:24 | 45918.5583 | 0.69118 | 0.0027166 | 177 | 45033 | Planned | Planned Interruption | Repalnting Poles 313474/312484 to correct depth
|  | O-7141-B | Whakapara |  | Hikurangi CB1112 | 2025-09-18 09:32 | 45918.3972 | 2025-09-18 13:16 | 45918.5528 | 0.7323 | 0.0032692 | 213 | 47712 | Planned | Planned Interruption | Tree Clearing Work from Pole 42797 towards Pole 312572
|  | O-7009-B | North River |  | Ruakaka CB7 | 2025-09-18 10:09 | 45918.4229 | 2025-09-18 11:54 | 45918.4958 | 0.14021 | 0.0013353 | 87 | 9135 | Planned | Planned Interruption | Replant pole 336417
|  | O-7198-B | Maunu |  | Maunu CB1032 | 2025-09-19 09:00 | 45919.3752 | 2025-09-19 13:39 | 45919.5687 | 0.89201 | 0.0033459 | 218 | 58118 | Planned | Planned Interruption | Replace LV crossarms
|  | F-10969-A | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-09-22 19:14 | 45922.8012 | 2025-09-22 21:50 | 45922.9097 | 0.11035 | 0.00070602 | 46 | 7190 | Unplanned | Vegetation | FP396854 - 2x HV Fuses blown @ L418. Patrolled - bamboo in line - cleared. Follow up required to clear bamboo through lines.
|  | O-6919-B | Town Dargaville |  | Dargaville CB3 | 2025-09-23 09:11 | 45923.3826 | 2025-09-23 16:38 | 45923.6931 | 2.0484 | 0.0046966 | 306 | 133459 | Planned | Planned Interruption | Pole, crossarms anf hardware replacements
|  | O-1216-C | Coast |  | Dargaville CB6 | 2025-09-24 08:07 | 45924.3382 | 2025-09-24 13:30 | 45924.5625 | 0.01983 | 6.1393e-05 | 4 | 1292 | Planned | Planned Interruption | Install 66kV pole. Went late due to work load.
|  | O-6916-B | Kaiwaka South |  | Kaiwaka CB1072 | 2025-09-24 09:01 | 45924.3758 | 2025-09-24 13:46 | 45924.5736 | 0.63823 | 0.0022408 | 146 | 41583 | Planned | Planned Interruption | Tree Clearing Work
|  | O-1219-C | Austin Road |  | Maunu CB1072 | 2025-09-24 09:06 | 45924.3792 | 2025-09-24 14:35 | 45924.6076 | 1.227 | 0.0037296 | 243 | 79947 | Planned | Planned Interruption | Repalce pole, hardware and straighten pole
|  | F-10972-A | Kamo Town |  | Kamo CB7 | 2025-09-24 12:35 | 45924.5241 | 2025-09-24 14:00 | 45924.5833 | 0.39129 | 0.015931 | 1038 | 25494 | Unplanned | Defective Equipment | 396920 / Hard fault causing Trip. Found to be HV fault between CB1 KMO & KL 7408.
|  | O-1177-C | Kensington |  | Alexander St CB8 | 2025-09-25 09:03 | 45925.3771 | 2025-09-25 14:07 | 45925.5882 | 0.38569 | 0.0012739 | 83 | 25129 | Planned | Planned Interruption | Isolate & Earth due to arm replacement requiring Tx removal & re-ins
|  | O-7147-B | Coast |  | Dargaville CB6 | 2025-09-25 09:32 | 45925.3972 | 2025-09-25 12:10 | 45925.5069 | 0.1552 | 0.00098229 | 64 | 10112 | Planned | Planned Interruption | Repalce 11kV cable and crucifix
|  | O-20479-A | Paparoa |  | Mareretu CB6 | 2025-09-25 09:35 | 45925.3993 | 2025-09-25 13:30 | 45925.5625 | 0.050496 | 0.00021488 | 14 | 3290 | Planned | Planned Interruption | Tree Clearing Work
|  | F-10975-A | Paparoa |  | Mareretu CB6 | 2025-09-25 17:29 | 45925.7284 | 2025-09-26 09:58 | 45926.4153 | 4.0988 | 0.0091015 | 593 | 267050 | Unplanned | Adverse Environment | FP 396963 - Replace pole and install stub pole due to bank giving way.
|  | F-10978-A | Te Kopuru |  | Dargaville CB2 | 2025-09-25 18:52 | 45925.7861 | 2025-09-25 21:44 | 45925.9056 | 0.901 | 0.028502 | 1857 | 58704 | Unplanned | Defective Equipment | Line down - FP396966
|  | O-1222-C | Tutukaka Block |  | Ngunguru CB1082 | 2025-09-26 09:08 | 45926.3806 | 2025-09-26 14:10 | 45926.5903 | 0.13055 | 0.0004451 | 29 | 8506 | Planned | Planned Interruption | Install new tele switch and remove switch 7201
|  | O-20485-A | Hotel |  | Poroti CB1052 | 2025-09-26 09:20 | 45926.3889 | 2025-09-26 15:07 | 45926.6299 | 0.14912 | 0.00042975 | 28 | 9716 | Planned | Planned Interruption | Install new automated switch and Remove SW 811
|  | O-1201-C | Hakaru |  | Kaiwaka CB1032 | 2025-09-26 09:40 | 45926.4028 | 2025-09-26 14:51 | 45926.6188 | 0.7876 | 0.0025325 | 165 | 51315 | Planned | Planned Interruption | Replace Pole 301912
|  | F-10984-A | Montgomery Ave |  | Onerahi CB8 | 2025-09-28 04:40 | 45928.1947 | 2025-09-28 08:57 | 45928.3729 | 0.61969 | 0.016054 | 1046 | 40375 | Unplanned | Wildlife | FP 397000 Line down nr pole 36359
|  | O-1228-C | Coast |  | Dargaville CB6 | 2025-09-29 08:33 | 45929.3563 | 2025-09-29 15:30 | 45929.6457 | 0.025586 | 6.1393e-05 | 4 | 1667 | Planned | Planned Interruption | Carrying out 66kV conductor works in proximity of existing 11kV
|  | O-1204-C | Kaka St |  | Whangarei South CB1032 | 2025-09-29 09:06 | 45929.3788 | 2025-09-29 10:03 | 45929.4185 | 0.12354 | 0.0021641 | 141 | 8049 | Planned | Planned Interruption | Remove 9169KL from network
|  | O-7069-B | Titoki |  | Poroti CB1032 | 2025-09-29 09:42 | 45929.4039 | 2025-09-29 15:11 | 45929.6327 | 0.3791 | 0.0011511 | 75 | 24700 | Planned | Planned Interruption | Repacing pole 50335
|  | O-1207-C | Whatatiri |  | Maungatapere CB8 | 2025-09-30 09:16 | 45930.3861 | 2025-09-30 14:42 | 45930.6125 | 0.073119 | 0.00023022 | 15 | 4764 | Planned | Planned Interruption | replace HV & LV x-arms and re-sag lines
|  | O-1150-C | Whatatiri |  | Maungatapere CB8 | 2025-09-30 09:31 | 45930.3968 | 2025-09-30 15:23 | 45930.6407 | 0.54437 | 0.0015502 | 101 | 35468 | Planned | Planned Interruption | Tree Clearing Work
|  | F-10999-A | Paranui |  | Tikipunga CB6 | 2025-09-30 21:37 | 45930.9006 | 2025-09-30 21:53 | 45930.9115 | 0.12478 | 0.011358 | 740 | 8130 | Unplanned | Unknown | E/F - 15 min close
|  | O-1231-C | Town Dargaville |  | Dargaville CB3 | 2025-09-30 22:02 | 45930.9181 | 2025-09-30 22:57 | 45930.9563 | 0.1242 | 0.0022715 | 148 | 8092 | Planned | Planned Interruption | Temp Reconfigure 11kV to reduce future outages - Cut break at Pole 32683
|  | O-7261-B | Coast |  | Dargaville CB6 | 2025-10-01 08:34 | 45931.3569 | 2025-10-01 12:57 | 45931.5396 | 0.016146 | 6.1393e-05 | 4 | 1052 | Planned | Planned Interruption | Isolate 11kV for safety to carry out 66kV conductor works
|  | O-7075-B | Bickerstaff |  | Maungaturoto CB2 | 2025-10-01 09:04 | 45931.3778 | 2025-10-01 15:10 | 45931.6319 | 0.51119 | 0.0013967 | 91 | 33306 | Planned | Planned Interruption | Network Maintenance - replace poles, hardware and transformers D277 & D271 like for like
|  | O-7093-B | Three Mile Bush |  | Kamo CB3 | 2025-10-02 09:24 | 45932.3917 | 2025-10-02 12:17 | 45932.5118 | 0.69036 | 0.0039905 | 260 | 44980 | Planned | Planned Interruption | Replace Hv and Lv hardware on pole #52552. Ran a little over time due to work load.
|  | F-11005-A | Turiwiri |  | Dargaville CB9 | 2025-10-02 11:03 | 45932.4604 | 2025-10-02 18:14 | 45932.7597 | 0.4575 | 0.01188 | 774 | 29808 | Unplanned | Wildlife | FP 397152 - Repair lines down (Pole 22881) & blown jumper (Pole 19020) which was caused by the lines down.
|  | F-11011-A | Ararua |  | Mareretu CB2 | 2025-10-02 13:28 | 45932.5609 | 2025-10-02 21:24 | 45932.8917 | 0.35924 | 0.0047273 | 308 | 23406 | Unplanned | Defective Equipment | FP 397157 - Replaced faulty TX
|  | O-1309-C | Jordan Valley |  | Hikurangi CB1102 | 2025-10-03 09:05 | 45933.3785 | 2025-10-03 10:55 | 45933.4549 | 0.0016883 | 1.5348e-05 | 1 | 110 | Planned | Planned Interruption | Resag 11kV conductors from Pole 35013 to EOL
|  | O-7078-B | ToeToe Rd |  | Kioreroa CB7 | 2025-10-03 09:07 | 45933.3799 | 2025-10-03 14:16 | 45933.5944 | 0.69242 | 0.0022408 | 146 | 45114 | Planned | Planned Interruption | Replace LV conductor
|  | O-1234-C | Town Dargaville |  | Dargaville CB3 | 2025-10-05 08:34 | 45935.3569 | 2025-10-05 16:57 | 45935.7063 | 2.6712 | 0.0053105 | 346 | 174038 | Planned | Planned Interruption | Pole, cross arms, switch replacment with Installtion of Temp Switch
|  | F-11020-A | ToeToe Rd |  | Kioreroa CB7 | 2025-10-06 01:08 | 45936.047 | 2025-10-06 01:23 | 45936.0577 | 0.10868 | 0.0094238 | 614 | 7081 | Unplanned | Unknown | Trip EF. 15 Min Close & BTN
|  | O-1267-C | Ararua |  | Mareretu CB2 | 2025-10-06 09:07 | 45936.3799 | 2025-10-06 14:01 | 45936.584 | 0.031587 | 0.00010744 | 7 | 2058 | Planned | Planned Interruption | Replace Xarms and hardware
|  | F-11023-A | Wairere |  | Mareretu CB5 | 2025-10-06 10:41 | 45936.445 | 2025-10-06 10:58 | 45936.4569 | 0.071953 | 0.0064309 | 419 | 4688 | Unplanned | Unknown | Fault beyond Sw 381 - remotely livened
|  | F-11029-A | Paranui |  | Tikipunga CB6 | 2025-10-06 11:57 | 45936.4981 | 2025-10-06 15:29 | 45936.6451 | 0.22603 | 0.011358 | 740 | 14727 | Unplanned | Third Party Interference | FP397243 Digger tangled in lines nr pole 51279
|  | O-7288-B | Coast |  | Dargaville CB6 | 2025-10-07 08:53 | 45937.3702 | 2025-10-07 17:03 | 45937.7102 | 0.33068 | 0.00067532 | 44 | 21545 | Planned | Planned Interruption | Install 66kV poles and replace conductor
|  | O-1294-C | Ararua |  | Mareretu CB2 | 2025-10-07 09:04 | 45937.3778 | 2025-10-07 14:08 | 45937.5889 | 0.05599 | 0.00018418 | 12 | 3648 | Planned | Planned Interruption | Network Maintenance - replace pole, x-arms, hardware and TX E214 like for like
|  | O-7090-B | Hotel |  | Poroti CB1052 | 2025-10-07 09:09 | 45937.3809 | 2025-10-07 13:31 | 45937.5629 | 0.11261 | 0.00042975 | 28 | 7337 | Planned | Planned Interruption | Repalce HV & LV crossarms. Fit solid linkt to L8281. Repl Tx W428
|  | F-11032-A | Ararua |  | Mareretu CB2 | 2025-10-07 12:14 | 45937.5096 | 2025-10-07 12:29 | 45937.5199 | 0.034303 | 0.0023022 | 150 | 2235 | Unplanned | Unknown | 15 min close
|  | F-11035-A | Tangaihi |  | Ruawai CB1032 | 2025-10-07 14:36 | 45937.608 | 2025-10-07 16:27 | 45937.6854 | 0.1349 | 0.0020106 | 131 | 8789 | Unplanned | Defective Equipment | FP 397270 - Line down on load side of insulator pole 28992 - corroded wire
|  | O-7282-B | Town Dargaville |  | Dargaville CB3 | 2025-10-07 22:03 | 45937.9187 | 2025-10-07 22:31 | 45937.9382 | 0.063603 | 0.0022715 | 148 | 4144 | Planned | Planned Interruption | Reinstate break & reconfigure 11kV feeder back to normal supply
|  | O-7273-B | Swamp South |  | Hikurangi CB1092 | 2025-10-08 09:04 | 45938.3778 | 2025-10-08 10:33 | 45938.4396 | 0.005464 | 6.1393e-05 | 4 | 356 | Planned | Planned Interruption | Replace hardware on pole #58256
|  | O-1273-C | Walton St |  | Whangarei South CB1022 | 2025-10-08 09:36 | 45938.4 | 2025-10-08 13:58 | 45938.5819 | 0.46253 | 0.0018111 | 118 | 30136 | Planned | Planned Interruption | re-attach HV cable to pole 419742
|  | O-1156-C | Alamein Ave |  | Onerahi CB3 | 2025-10-09 09:01 | 45939.3757 | 2025-10-09 14:13 | 45939.5924 | 0.80449 | 0.0025785 | 168 | 52416 | Planned | Planned Interruption | Replace Pole 38017
|  | O-1276-C | North River |  | Ruakaka CB7 | 2025-10-09 09:05 | 45939.3785 | 2025-10-09 14:48 | 45939.6167 | 0.026322 | 7.6741e-05 | 5 | 1715 | Planned | Planned Interruption | Replace Pole 43893
|  | F-11053-A |  |  | Dargaville CB38 | 2025-10-10 03:37 | 45940.1507 | 2025-10-10 05:49 | 45940.2426 | 5.464 | 0.043482 | 2833 | 356000 | Unplanned | Defective Equipment | FP 397356 CB38 DAR Trip, loss of CB1,2,3,4. Loss of DC & comms. IW sent to site. 16A Battery Isol CB tripped. Relay fault
|  | O-1315-C | Alamein Ave |  | Onerahi CB3 | 2025-10-10 09:00 | 45940.375 | 2025-10-10 13:56 | 45940.5806 | 0.69693 | 0.0029469 | 192 | 45408 | Planned | Planned Interruption | Remove Sw 9409 and Install New Sw 10333
|  | O-1291-C | North River |  | Ruakaka CB7 | 2025-10-10 09:28 | 45940.3944 | 2025-10-10 14:27 | 45940.6021 | 0.013767 | 4.6045e-05 | 3 | 897 | Planned | Planned Interruption | Replace crossarm @ Pole 44015
|  | F-11059-A | Coast |  | Dargaville CB6 | 2025-10-11 02:09 | 45941.0894 | 2025-10-11 02:23 | 45941.0995 | 0.15224 | 0.016085 | 1048 | 9919 | Unplanned | Unknown | OC NO FPI's activated
|  | O-7351-B | Treatment |  | Kioreroa CB2 | 2025-10-12 09:09 | 45942.3812 | 2025-10-12 11:27 | 45942.4771 | 0.027535 | 0.00019953 | 13 | 1794 | Planned | Planned Interruption | Remove KL993 from network
|  | O-1318-C | Kensington |  | Alexander St CB8 | 2025-10-13 09:08 | 45943.3806 | 2025-10-13 14:14 | 45943.5931 | 0.58237 | 0.0019032 | 124 | 37944 | Planned | Planned Interruption | Replace HV & LV hardware.
|  | O-1327-C | North River |  | Ruakaka CB7 | 2025-10-14 09:00 | 45944.3752 | 2025-10-14 15:12 | 45944.6333 | 0.38209 | 0.0010283 | 67 | 24895 | Planned | Planned Interruption | Replace pole
|  | O-1336-C | Ararua |  | Mareretu CB2 | 2025-10-14 09:33 | 45944.3979 | 2025-10-14 13:32 | 45944.5639 | 0.073365 | 0.00030697 | 20 | 4780 | Planned | Planned Interruption | Tree Clearing Work
|  | O-1321-C | King Road |  | Mangawhai North CB2 | 2025-10-15 09:08 | 45945.3806 | 2025-10-15 15:06 | 45945.6292 | 1.3018 | 0.0036375 | 237 | 84818 | Planned | Planned Interruption | Replace pole 33010-33009
|  | F-11095-A | Ruatangata |  | Kamo CB6 | 2025-10-15 16:58 | 45945.7067 | 2025-10-15 18:53 | 45945.7868 | 0.37017 | 0.0067379 | 439 | 24118 | Unplanned | Unknown | 397495 - Tripped B&C phase O/C, closed in sections, unknown cause.
|  | O-20785-A | Bickerstaff |  | Maungaturoto CB2 | 2025-10-16 09:06 | 45946.3792 | 2025-10-16 13:52 | 45946.5778 | 0.14486 | 0.00050649 | 33 | 9438 | Unplanned | Defective Equipment | Urgent Repairs - replace H structure pole 16226/56189
|  | O-1339-C | North Dargaville |  | Dargaville CB1 | 2025-10-16 09:08 | 45946.3806 | 2025-10-16 13:01 | 45946.5424 | 0.017881 | 7.6741e-05 | 5 | 1165 | Planned | Planned Interruption | Replace Poles 24018, 24019, 24020
|  | O-1345-C | Ararua |  | Mareretu CB2 | 2025-10-16 09:34 | 45946.3986 | 2025-10-16 13:14 | 45946.5514 | 0.084415 | 0.00038371 | 25 | 5500 | Planned | Planned Interruption | Tree Cutting
|  | O-20869-A | Tangaihi |  | Ruawai CB1032 | 2025-10-16 12:18 | 45946.5128 | 2025-10-16 13:22 | 45946.5567 | 0.16776 | 0.0027013 | 176 | 10930 | Unplanned | Lightning | Planned G & B turned into an urgent shutdown when Marc found 2 x blown LA's Also faulty bypass Sw
|  | O-7294-B | Maunu Road |  | Whangarei South CB1102 | 2025-10-17 09:04 | 45947.3778 | 2025-10-17 13:01 | 45947.5424 | 0.24467 | 0.0010437 | 68 | 15941 | Planned | Planned Interruption | Replace LV x-arms between poles 40715 and 40720
|  | O-7318-B | Water Treatment |  | Kioreroa CB2 | 2025-10-19 09:03 | 45949.3771 | 2025-10-19 12:09 | 45949.5062 | 0.011419 | 6.1393e-05 | 4 | 744 | Planned | Planned Interruption | Replace pole
|  | O-7411-B | Water Treatment |  | Kioreroa CB2 | 2025-10-19 09:04 | 45949.3778 | 2025-10-19 13:36 | 45949.5667 | 0.12942 | 0.0004758 | 31 | 8432 | Planned | Planned Interruption | Liven New Tx WO319 & remove WO251. Liven New RMU.
|  | O-7126-B | Norfolk St |  | Alexander St CB1 | 2025-10-19 09:08 | 45949.3803 | 2025-10-19 14:17 | 45949.5948 | 0.055683 | 0.00055254 | 36 | 3628 | Planned | Planned Interruption | CB maintenance and time testing. Ran over time due to malfunction on mechanical open & close function.
|  | O-1183-C | Tamaterau |  | Onerahi CB7 | 2025-10-20 09:11 | 45950.3826 | 2025-10-20 12:21 | 45950.5146 | 0.09915 | 0.00052184 | 34 | 6460 | Planned | Planned Interruption | Replace Transformer 00123 Like for Like
|  | O-7408-B | Rewa Rewa Rd |  | Whangarei South CB1082 | 2025-10-22 09:05 | 45952.3785 | 2025-10-22 14:03 | 45952.5854 | 0.018295 | 6.1393e-05 | 4 | 1192 | Planned | Planned Interruption | Tree Clearing Work
|  | O-7393-B | North Dargaville |  | Dargaville CB1 | 2025-10-22 09:07 | 45952.3799 | 2025-10-22 15:34 | 45952.6486 | 0.053458 | 0.00013813 | 9 | 3483 | Planned | Planned Interruption | Repalce Poles and Tx M236 like for like
|  | O-1258-C | Kamo Town |  | Kamo CB7 | 2025-10-22 13:19 | 45952.5549 | 2025-10-22 14:20 | 45952.5972 | 0.053366 | 0.00087485 | 57 | 3477 | Planned | Planned Interruption | Fit neutral lugs
|  | F-11140-A | North Dargaville |  | Dargaville CB1 | 2025-10-22 17:03 | 45952.7104 | 2025-10-22 18:44 | 45952.7806 | 0.040305 | 0.00039905 | 26 | 2626 | Unplanned | Defective Equipment | FP 397678 Repaired spragged 11kV conductors between poles 345950 & 27443
|  | O-1342-C | Otangarei |  | Tikipunga CB7 | 2025-10-23 08:51 | 45953.3688 | 2025-10-23 14:42 | 45953.6125 | 0.52795 | 0.0015041 | 98 | 34398 | Planned | Planned Interruption | Network Maintenance isolation to remove LV epoxy Joints. LV Fuses at KT176 to dangerous to open
|  | O-7396-B | Te Hihi |  | Maunu CB1022 | 2025-10-23 09:09 | 45953.3812 | 2025-10-23 14:48 | 45953.6167 | 0.3434 | 0.001013 | 66 | 22374 | Planned | Planned Interruption | Replacing TX pole S237, Fix Guy at pole 58657
|  | O-7321-B | Titoki |  | Poroti CB1032 | 2025-10-23 09:31 | 45953.3962 | 2025-10-23 12:35 | 45953.5244 | 0.065199 | 0.00035301 | 23 | 4248 | Planned | Planned Interruption | Tree Clearing Work- Tree clearing work between poles 50745 to pole 50741.
|  | O-20857-A | Titoki |  | Poroti CB1032 | 2025-10-23 09:37 | 45953.4007 | 2025-10-23 14:31 | 45953.6049 | 0.036099 | 0.00012279 | 8 | 2352 | Planned | Planned Interruption | Removed KL9132. Found broken x-arm outside work area. Same amount of customers, 2.5hrs over planned end time.
|  | F-11155-A | Matapouri |  | Ngunguru CB1032 | 2025-10-24 02:21 | 45954.0976 | 2025-10-24 09:41 | 45954.4035 | 1.6706 | 0.013936 | 908 | 108845 | Unplanned | Defective Equipment | Replaced 2 cracked insulators. B phase
|  | F-11158-A | Coast |  | Dargaville CB6 | 2025-10-24 17:38 | 45954.7347 | 2025-10-24 19:48 | 45954.8253 | 0.06741 | 0.0013353 | 87 | 4392 | Unplanned | Lightning | 397749/ Faulty HV Fuses. Top of DDO's burnt, possibly lightning from previous day
|  | F-11164-A | Marsden South |  | Bream Bay CB1111 | 2025-10-25 20:06 | 45955.8373 | 2025-10-25 20:21 | 45955.8481 | 0.024419 | 0.0015809 | 103 | 1591 | Unplanned | Unknown | Trip OC Phase BC
|  | F-11170-A | Jordan Valley |  | Hikurangi CB1102 | 2025-10-27 15:59 | 45957.6661 | 2025-10-28 05:44 | 45958.2387 | 0.82155 | 0.0073672 | 480 | 53527 | Unplanned | Vegetation | FP 397770 - Replace poles 35032 & 35033
|  | F-11176-A | Coast |  | Dargaville CB6 | 2025-10-28 00:27 | 45958.0186 | 2025-10-28 00:41 | 45958.0287 | 0.062667 | 0.016039 | 1045 | 4083 | Unplanned | Lightning | Fault area between Sw 2025, 2120 & Rec 1550 FPI's @ 2025 activated_ Closed after 15 mins
|  | F-11179-A | KEN - TIK A |  | Kensington CB6 | 2025-10-28 00:56 | 45958.0385 | 2025-10-28 01:49 | 45958.0755 | 7.2693 | 0.22016 | 14344 | 473625 | Unplanned | Lightning | 397776/ Trip KEN CB3042/TIK CB112 & ALX CB52. All ICP's from ALX & TIK. CT phasing incorrect CB 3042 TIK & no comms CB 6 TIK.
|  | F-11215-A | Puwera |  | Maungatapere CB7 | 2025-10-28 12:17 | 45958.5119 | 2025-10-28 19:01 | 45958.7924 | 0.62589 | 0.0041287 | 269 | 40779 | Unplanned | Vegetation | 397817 / Isolate to repair Lines down past Pole 76026 due to vegetation
|  | F-11224-A | Mata |  | Ruakaka CB3 | 2025-10-28 12:31 | 45958.5215 | 2025-10-28 17:26 | 45958.7264 | 0.53501 | 0.016868 | 1099 | 34858 | Unplanned | Defective Equipment | FP 397828 - Repair broken guy wire
|  | F-11230-A | Matapouri |  | Ngunguru CB1032 | 2025-10-28 13:15 | 45958.5518 | 2025-10-28 20:06 | 45958.8375 | 2.7103 | 0.016868 | 1099 | 176584 | Unplanned | Defective Equipment | 397832 / Isolate to repair Lines down between poles 349839 & 59022.
|  | F-11236-A | Cairnfield Rd |  | Tikipunga CB5 | 2025-10-28 13:54 | 45958.5792 | 2025-10-28 21:56 | 45958.9139 | 1.42 | 0.018172 | 1184 | 92517 | Unplanned | Third Party Interference | 397822 / Car Vs Tx WC153. LV backfeed to restore customers at 2156hrs 28/10.
|  | F-11239-A | Coast |  | Dargaville CB6 | 2025-10-28 14:45 | 45958.6146 | 2025-10-29 18:07 | 45959.7549 | 0.025202 | 1.5348e-05 | 1 | 1642 | Unplanned | Lightning | 397821 / Replaced TX L106 & LAs Pole 328246
|  | F-11248-A | Tangowahine |  | Dargaville CB8 | 2025-10-28 15:33 | 45958.6479 | 2025-10-29 12:25 | 45959.5174 | 0.23145 | 0.0049114 | 320 | 15080 | Unplanned | Vegetation | 397838 / Tree fell causing LV & HV clash at pole 37883. Un tangled with line stick remaining outside MADS.
|  | F-11263-A | Puwera |  | Maungatapere CB7 | 2025-10-28 16:51 | 45958.7024 | 2025-10-28 22:00 | 45958.9167 | 0.42202 | 0.0066151 | 431 | 27496 | Unplanned | Vegetation | 397850 / Lines down repairs at pole 46803 (SW 884 open @ time of tripping)
|  | F-11266-A | Paparoa |  | Mareretu CB6 | 2025-10-28 17:48 | 45958.7418 | 2025-10-29 00:03 | 45959.0021 | 1.798 | 0.0091015 | 593 | 117149 | Unplanned | Vegetation | 397855 / Isolate to repair lines down at pole 13607.
|  | F-11272-A | Whakapara |  | Hikurangi CB1112 | 2025-10-29 02:52 | 45959.1194 | 2025-10-29 04:56 | 45959.2056 | 0.034257 | 0.00027627 | 18 | 2232 | Unplanned | Adverse Environment | 397865 / Isolated for House fire under lines at Tx KB505
|  | O-18364-A | Swamp North |  | Hikurangi CB1042 | 2025-10-29 09:05 | 45959.3785 | 2025-10-29 12:10 | 45959.5069 | 0.13345 | 0.00072137 | 47 | 8695 | Planned | Planned Interruption | Hardware replacements
|  | O-7432-B | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-10-29 09:07 | 45959.3799 | 2025-10-29 13:37 | 45959.5674 | 0.26107 | 0.00096694 | 63 | 17010 | Planned | Planned Interruption | Replace poles, conductor and pole hardware
|  | F-11275-A | Whatatiri |  | Maungatapere CB8 | 2025-10-29 10:29 | 45959.4368 | 2025-10-29 12:25 | 45959.5174 | 0.039583 | 0.00039905 | 26 | 2579 | Unplanned | Lightning | FP 397868 - Replace faulty DDO
|  | F-11284-A | Tangaihi |  | Ruawai CB1032 | 2025-10-30 01:58 | 45960.0821 | 2025-10-30 05:56 | 45960.2472 | 0.42682 | 0.010529 | 686 | 27809 | Unplanned | Wildlife | 397913 / Possum found at pole 16059 resting on centre phase. Removed & BTN
|  | O-7324-B | Maunu |  | Maunu CB1032 | 2025-10-30 09:14 | 45960.3847 | 2025-10-30 15:42 | 45960.6542 | 0.1727 | 0.0004451 | 29 | 11252 | Planned | Planned Interruption | Replace HV / Lv crossarms, Tx S207 and Hardware
|  | O-20836-A | Te Kopuru |  | Dargaville CB2 | 2025-10-30 09:16 | 45960.3861 | 2025-10-30 14:10 | 45960.5902 | 0.30225 | 0.0010283 | 67 | 19693 | Planned | Planned Interruption | New pole and transformer to be installed and Pole replacement
|  | F-11290-A | Whakapara |  | Hikurangi CB1112 | 2025-10-30 12:15 | 45960.5107 | 2025-10-30 14:26 | 45960.6017 | 0.036191 | 0.00027627 | 18 | 2358 | Unplanned | Adverse Environment | FP 397925 - Replace burnt crossarm
|  | O-20809-A | Puwera |  | Maungatapere CB7 | 2025-10-31 09:02 | 45961.3767 | 2025-10-31 12:28 | 45961.5196 | 0.18315 | 0.0008902 | 58 | 11933 | Planned | Planned Interruption | Installing & Automating New Switch 3985 on pole 46677. Removing Switch 8572 G&B.
|  | O-1261-C | Tamaterau |  | Onerahi CB7 | 2025-10-31 09:07 | 45961.3799 | 2025-10-31 15:38 | 45961.6514 | 0.63012 | 0.0016116 | 105 | 41055 | Planned | Planned Interruption | Replace TX OO107 and HV fuses
|  | O-20812-A | Forum North |  | Alexander St CB2 | 2025-11-02 08:39 | 45963.3604 | 2025-11-02 20:18 | 45963.8458 | 0.010728 | 1.5348e-05 | 1 | 699 | Planned | Planned Interruption | Replace RMU 222/223/224 LV backfed excl 1 ICP with own GEN.
|  | F-11311-A | Whangarei Heads |  | Parua Bay CB3 | 2025-11-02 21:18 | 45963.8873 | 2025-11-03 11:45 | 45964.4896 | 4.8667 | 0.02115 | 1378 | 317082 | Unplanned | Third Party Interference | FP 398001 Car vs pole 326604. Also replace cracked pole 24474. Sw 977 FPI did not indicate fault.
|  | O-7297-B | Titoki |  | Poroti CB1032 | 2025-11-03 09:25 | 45964.3924 | 2025-11-03 14:35 | 45964.6076 | 0.04758 | 0.00015348 | 10 | 3100 | Planned | Planned Interruption | Tx upgrade
|  | F-11320-A | North Dargaville |  | Dargaville CB1 | 2025-11-03 13:02 | 45964.5431 | 2025-11-03 14:23 | 45964.5993 | 0.032323 | 0.00039905 | 26 | 2106 | Unplanned | Defective Equipment | 398024/ King bolt failure (nut came off, bolt in good condition)
|  | F-11323-A | Town Hikurangi |  | Hikurangi CB1082 | 2025-11-03 14:27 | 45964.602 | 2025-11-03 14:45 | 45964.6145 | 0.23498 | 0.013031 | 849 | 15310 | Unplanned | Unknown | Trip OC, Phase ABC involved in fault
|  | F-11326-A | Titoki |  | Poroti CB1032 | 2025-11-03 22:09 | 45964.9228 | 2025-11-04 05:00 | 45965.2083 | 0.19227 | 0.0023176 | 151 | 12527 | Unplanned | Third Party Interference | Replaced pole hit by tractor FP 398043
|  | O-20971-A | Swamp South |  | Hikurangi CB1092 | 2025-11-04 09:00 | 45965.3753 | 2025-11-04 14:44 | 45965.6142 | 0.25314 | 0.00073672 | 48 | 16493 | Planned | Planned Interruption | Tree Clearing Work
|  | O-18367-A | Tangowahine |  | Dargaville CB8 | 2025-11-04 09:08 | 45965.3806 | 2025-11-04 13:36 | 45965.5667 | 0.08638 | 0.00032231 | 21 | 5628 | Planned | Planned Interruption | Crossarm replacements (Pole replacement didnt go ahead due to access issues)
|  | O-20848-A | Maunu Mountain |  | Maungatapere CB1 | 2025-11-05 09:01 | 45966.3755 | 2025-11-05 13:46 | 45966.5736 | 0.21896 | 0.00076741 | 50 | 14266 | Planned | Planned Interruption | Replacing HV & LV Cross arms.
|  | O-20890-A | Paparoa |  | Mareretu CB6 | 2025-11-05 09:08 | 45966.3806 | 2025-11-05 15:17 | 45966.6368 | 0.20955 | 0.00056789 | 37 | 13653 | Planned | Planned Interruption | Replace pole, hardware, replace transformer Y184 with a 50kva and replace HV lines with fluorine between poles 21011 and 31580
|  | O-20911-A | Tamaterau |  | Onerahi CB7 | 2025-11-06 09:05 | 45967.3785 | 2025-11-06 15:24 | 45967.6417 | 1.2856 | 0.003392 | 221 | 83759 | Planned | Planned Interruption | Tree Clearing Work
|  | O-20896-A | Hokianga Rd |  | Dargaville CB7 | 2025-11-06 09:06 | 45967.3792 | 2025-11-06 14:45 | 45967.6146 | 1.6129 | 0.004758 | 310 | 105090 | Planned | Planned Interruption | Haul new 11kV cable from Pole 304905 to new TX DA143
|  | O-21106-A | Whau Valley |  | Tikipunga CB1 | 2025-11-06 09:10 | 45967.3819 | 2025-11-06 13:12 | 45967.55 | 0.21914 | 0.00090555 | 59 | 14278 | Planned | Planned Interruption | Upgrade Tx WC167
|  | O-20956-A | Waipu |  | Ruakaka CB2 | 2025-11-06 09:12 | 45967.3833 | 2025-11-06 13:43 | 45967.5715 | 0.095666 | 0.00035301 | 23 | 6233 | Planned | Planned Interruption | Tx POLE REPLACEMENT, LV ARM & WIRE REPLACEMENT
|  | O-20899-A | Te Kopuru |  | Dargaville CB2 | 2025-11-06 09:38 | 45967.4014 | 2025-11-06 14:44 | 45967.6139 | 0.028179 | 9.209e-05 | 6 | 1836 | Planned | Planned Interruption | Pole hardware replacement
|  | F-11335-A | Turiwiri |  | Dargaville CB9 | 2025-11-06 10:11 | 45967.4243 | 2025-11-06 11:37 | 45967.4841 | 0.073994 | 0.0008595 | 56 | 4821 | Unplanned | Defective Equipment | FP398094 - Replace corroded/broken HV pin insulator at pole 47282
|  | O-20851-A | Maunu Road |  | Whangarei South CB1102 | 2025-11-07 09:04 | 45968.3778 | 2025-11-07 11:17 | 45968.4701 | 0.88593 | 0.0066611 | 434 | 57722 | Planned | Planned Interruption | Replace Hv arm, DDO's and hardware on pole #35545
|  | F-11341-A | Access Rd |  | Ruawai CB1022 | 2025-11-08 15:58 | 45969.665 | 2025-11-08 16:58 | 45969.7069 | 0.16966 | 0.0051263 | 334 | 11054 | Unplanned | Lightning | FP 398185 - lightning strike E351
|  | O-21190-A | Marsden Bay |  | Bream Bay CB1107 | 2025-11-09 09:30 | 45970.3958 | 2025-11-09 15:10 | 45970.6319 | 0.0096847 | 6.1393e-05 | 4 | 631 | Planned | Planned Interruption | Connect RO446 amd RO450 to new switches respectively. Isolated Txs again due to wrong phase rotation
|  | O-20914-A | Union East |  | Kioreroa CB1 | 2025-11-09 20:11 | 45970.841 | 2025-11-10 04:24 | 45971.1834 | 0.15892 | 0.00032231 | 21 | 10354 | Planned | Planned Interruption | Transformer Upgrade
|  | O-1195-C | Springs Flat |  | Kamo CB1 | 2025-11-10 09:43 | 45971.4047 | 2025-11-10 13:33 | 45971.5645 | 0.33904 | 0.0014734 | 96 | 22090 | Planned | Planned Interruption | Refurbish Dsub KS173, replace HV fuses on Dsub KS381 (pole replacements didn't go ahead due to access issues)
|  | O-20824-A | Maungatapere - Dairy Factory |  | Maungatapere CB6 | 2025-11-11 09:04 | 45972.3778 | 2025-11-11 14:25 | 45972.6007 | 0.0098536 | 3.0697e-05 | 2 | 642 | Planned | Planned Interruption | Connect new 11kv cable and liven new 50kva transformer O278.
|  | O-18421-A | Titoki |  | Poroti CB1032 | 2025-11-11 09:05 | 45972.3785 | 2025-11-11 13:41 | 45972.5701 | 0.088958 | 0.00032231 | 21 | 5796 | Planned | Planned Interruption | Replace HV and LV crossarms
|  | O-20818-A | Dunns Rd |  | Ruawai CB1082 | 2025-11-11 10:04 | 45972.4194 | 2025-11-11 15:10 | 45972.6319 | 0.23952 | 0.00078276 | 51 | 15606 | Planned | Planned Interruption | Tree Clearing Work
|  | O-20842-A | Otangarei |  | Tikipunga CB7 | 2025-11-12 09:21 | 45973.3896 | 2025-11-12 11:43 | 45973.4882 | 0.13295 | 0.00093624 | 61 | 8662 | Planned | Planned Interruption | Bolt down Tx KK106
|  | O-20887-A | One Tree Point |  | Ruakaka CB6 | 2025-11-12 09:36 | 45973.4 | 2025-11-12 13:47 | 45973.5743 | 0.43532 | 0.0017344 | 113 | 28363 | Planned | Planned Interruption | Tree Clearing Work
|  | F-11365-A | North River |  | Ruakaka CB7 | 2025-11-12 18:52 | 45973.7861 | 2025-11-13 02:08 | 45974.0889 | 1.2767 | 0.022669 | 1477 | 83180 | Unplanned | Vegetation | Trees in lines between poles 43662 & 43663. FP398304
|  | O-20980-A | Hakaru |  | Kaiwaka CB1032 | 2025-11-13 09:07 | 45974.3795 | 2025-11-13 15:25 | 45974.6423 | 0.092934 | 0.00024557 | 16 | 6055 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | O-21097-A | King Road |  | Mangawhai North CB2 | 2025-11-13 09:07 | 45974.3799 | 2025-11-13 14:48 | 45974.6167 | 0.52338 | 0.0015348 | 100 | 34100 | Planned | Planned Interruption | Network Maintenance - Replace pole 33472, replace pole 33473 and relocate and replace transformer MC235 and relabel MC595
|  | O-20953-A | Langs Beach |  | Mangawhai North CB3 | 2025-11-13 09:28 | 45974.3944 | 2025-11-13 12:58 | 45974.5403 | 0.0032231 | 1.5348e-05 | 1 | 210 | Planned | Planned Interruption | Replace SW 8090
|  | O-20959-A | Otonga |  | Hikurangi CB1032 | 2025-11-13 09:39 | 45974.4021 | 2025-11-13 15:01 | 45974.6257 | 0.10873 | 0.00033766 | 22 | 7084 | Planned | Planned Interruption | Tree Clearing Work
|  | F-11383-A | North River |  | Ruakaka CB7 | 2025-11-13 14:57 | 45974.6229 | 2025-11-13 16:31 | 45974.688 | 0.16541 | 0.001765 | 115 | 10777 | Unplanned | Defective Equipment | FP: 398338 Broken HV jumper to HV Fuses RB140
|  | F-11389-A | Marsden South |  | Bream Bay CB1111 | 2025-11-13 18:33 | 45974.7731 | 2025-11-13 18:48 | 45974.7836 | 0.02379 | 0.0015809 | 103 | 1550 | Unplanned | Unknown | Trip Overcurrent B & C. 15 Min close & BTN
|  | F-11392-A | Paparoa |  | Mareretu CB6 | 2025-11-14 10:48 | 45975.45 | 2025-11-14 11:32 | 45975.4806 | 0.28229 | 0.0064156 | 418 | 18392 | Unplanned | Third Party Interference | 398357 - Car/trailer Vs pole 912528
|  | F-11398-A | Kiripaka Rd |  | Tikipunga CB8 | 2025-11-15 07:34 | 45976.3156 | 2025-11-15 18:30 | 45976.7708 | 2.4309 | 0.0078583 | 512 | 158382 | Unplanned | Third Party Interference | FP 398384 - Replace Pole 307141
|  | F-11401-A | Access Rd |  | Ruawai CB1022 | 2025-11-15 14:02 | 45976.5847 | 2025-11-15 14:16 | 45976.5944 | 0.00064463 | 4.6045e-05 | 3 | 42 | Unplanned | Unknown | FP398386 - Found 1x HV fuse blown, removed remaining 2x fuses. Reloaded and closed.
|  | F-11404-A | Swamp North |  | Hikurangi CB1042 | 2025-11-15 17:26 | 45976.7266 | 2025-11-16 01:34 | 45977.0653 | 1.299 | 0.0039445 | 257 | 84633 | Unplanned | Third Party Interference | FP 398388 - Replace Pole 38572
|  | O-21322-A | Fert. Works |  | Kioreroa CB6 | 2025-11-16 08:45 | 45977.3646 | 2025-11-16 16:15 | 45977.6771 | 0.013813 | 3.0697e-05 | 2 | 900 | Planned | Planned Interruption | Repair damaged cable and bolt down TX
|  | O-21052-A | Hakaru |  | Kaiwaka CB1032 | 2025-11-18 09:01 | 45979.376 | 2025-11-18 15:14 | 45979.6351 | 0.61256 | 0.0016423 | 107 | 39911 | Planned | Planned Interruption | Replace Poles and hardware
|  | O-21637-A | Treatment |  | Kioreroa CB2 | 2025-11-18 19:37 | 45979.8174 | 2025-11-18 20:21 | 45979.8479 | 0.058584 | 0.0034534 | 225 | 3817 | Unplanned | Defective Equipment | FP 398458 - CB2 KIO opened - FENZ fire call reporting Tx on fire by truckstop. Burnt rodent in Tx LV & LV cable fault
|  | O-21262-A | Hatea Drive |  | Tikipunga CB3 | 2025-11-19 09:09 | 45980.3812 | 2025-11-19 12:04 | 45980.5028 | 0.11281 | 0.00064463 | 42 | 7350 | Planned | Planned Interruption | Replace crossarm
|  | O-21547-A | Pataua |  | Parua Bay CB1 | 2025-11-19 10:14 | 45980.4265 | 2025-11-19 14:44 | 45980.6137 | 0.26493 | 0.00098229 | 64 | 17261 | Planned | Planned Interruption | Replace crossarm Pole 23853
|  | F-11419-A | North Dargaville |  | Dargaville CB1 | 2025-11-19 14:55 | 45980.6215 | 2025-11-19 15:49 | 45980.659 | 0.036467 | 0.00067532 | 44 | 2376 | Unplanned | Defective Equipment | FP398483 / Isolate to repair Broken Binder at Pole 27351.
|  | F-11422-A | Te Hihi |  | Maunu CB1022 | 2025-11-19 21:18 | 45980.8874 | 2025-11-20 07:13 | 45981.3007 | 0.89384 | 0.0055714 | 363 | 58237 | Unplanned | Defective Equipment | FP398500 / Cable Fault, Arcing across phases at pole 58657 joint. No Obvious cause found on site.
|  | O-7096-B | Wharekohe |  | Poroti CB1062 | 2025-11-20 09:13 | 45981.384 | 2025-11-20 14:08 | 45981.5889 | 0.33505 | 0.0011358 | 74 | 21830 | Planned | Planned Interruption | Repalce Pole, crossarms and refurbish Dsub
|  | O-21022-A | Titoki |  | Poroti CB1032 | 2025-11-20 09:32 | 45981.3969 | 2025-11-20 14:24 | 45981.6001 | 0.10329 | 0.00035301 | 23 | 6730 | Planned | Planned Interruption | Tree Clearing Work
|  | O-21271-A | King Road |  | Mangawhai North CB2 | 2025-11-20 10:00 | 45981.4167 | 2025-11-20 12:34 | 45981.5236 | 0.0094545 | 6.1393e-05 | 4 | 616 | Planned | Planned Interruption | Upgrade Tx MC421 to 3ph 50kva and connect new LV cable & pillars
|  | O-21202-A | Hakaru |  | Kaiwaka CB1032 | 2025-11-21 09:01 | 45982.3757 | 2025-11-21 12:20 | 45982.5139 | 0.27794 | 0.0013967 | 91 | 18109 | Planned | Planned Interruption | Repalce poles and hardware
|  | O-21004-A | North Kaiwaka |  | Kaiwaka CB1022 | 2025-11-21 09:09 | 45982.3812 | 2025-11-21 15:17 | 45982.6368 | 0.20898 | 0.00056789 | 37 | 13616 | Planned | Planned Interruption | Upgrade Tx C431
|  | F-11434-A | Te Kopuru |  | Dargaville CB2 | 2025-11-21 12:40 | 45982.5278 | 2025-11-21 12:59 | 45982.541 | 0.0023329 | 0.00012279 | 8 | 152 | Unplanned | Defective Equipment | 398539 - Found 1x HV fuse blown/corroded, replaced all 3
|  | F-11446-A | Otonga |  | Hikurangi CB1032 | 2025-11-23 18:31 | 45984.7714 | 2025-11-23 19:29 | 45984.8121 | 0.25708 | 0.0043896 | 286 | 16750 | Unplanned | Defective Equipment | 398556 - Reported line down, FPI activated (no tripping), opened Sw for safety, LV line down @ Tx KS230
|  | O-20989-A | Coast |  | Dargaville CB6 | 2025-11-24 08:36 | 45985.358 | 2025-11-24 14:45 | 45985.6148 | 0.028364 | 7.6741e-05 | 5 | 1848 | Planned | Planned Interruption | Install 66KV poles and conductor
|  | O-21337-A | Matapouri |  | Ngunguru CB1032 | 2025-11-24 09:35 | 45985.3994 | 2025-11-24 14:38 | 45985.6095 | 0.17632 | 0.00064463 | 42 | 11488 | Planned | Planned Interruption | Replace poles & Tx
|  | O-21247-A | Kaiatea |  | Ngunguru CB1072 | 2025-11-25 09:10 | 45986.3819 | 2025-11-25 16:07 | 45986.6715 | 0.40865 | 0.0013353 | 87 | 26625 | Planned | Planned Interruption | Replacing Transformer Pole NP155 (59269). Delay on restore for some ICP's due to broken new pole. Reinterruption for tap change
|  | O-21496-A | Taipuha |  | Mareretu CB1 | 2025-11-25 09:19 | 45986.3882 | 2025-11-25 12:51 | 45986.5354 | 0.30261 | 0.0014274 | 93 | 19716 | Planned | Planned Interruption | Replace Poles and hardware
|  | F-11464-A | Bank of NZ |  | Alexander St CB6 | 2025-11-25 19:20 | 45986.8056 | 2025-11-25 21:17 | 45986.8868 | 0.14905 | 0.0012739 | 83 | 9711 | Unplanned | Third Party Interference | FP 398628 - car vs LV pole 33540. Made safe & livened HV & partial LV to replace pole
|  | O-21208-A | Hakaru |  | Kaiwaka CB1032 | 2025-11-26 09:01 | 45987.3758 | 2025-11-26 13:48 | 45987.5747 | 0.070326 | 0.00024557 | 16 | 4582 | Planned | Planned Interruption | Replacing overhead conductors
|  | O-21205-A | Taipuha |  | Mareretu CB1 | 2025-11-26 09:10 | 45987.3819 | 2025-11-26 14:55 | 45987.6215 | 0.23828 | 0.00069067 | 45 | 15525 | Planned | Planned Interruption | Replace pole
|  | F-11479-A | ToeToe Rd |  | Kioreroa CB7 | 2025-11-26 18:47 | 45987.7826 | 2025-11-26 19:52 | 45987.8278 | 0.2514 | 0.0038678 | 252 | 16380 | Unplanned | Wildlife | FP 398666 repair spragged 11kV - possbile bird strike
|  | O-21100-A | Tikipunga Hill |  | Tikipunga CB4 | 2025-11-27 09:06 | 45988.3792 | 2025-11-27 15:21 | 45988.6396 | 0.3626 | 0.00096694 | 63 | 23625 | Planned | Planned Interruption | Reaplce pole and upgrade TX TT155
|  | O-21295-A | Te Kopuru |  | Dargaville CB2 | 2025-11-27 12:02 | 45988.5014 | 2025-11-27 14:15 | 45988.5938 | 0.13276 | 0.00099764 | 65 | 8650 | Planned | Planned Interruption | Relocate transformer
|  | F-11482-A | Mata |  | Ruakaka CB3 | 2025-11-27 16:35 | 45988.6908 | 2025-11-27 21:40 | 45988.9028 | 0.45211 | 0.0029008 | 189 | 29457 | Unplanned | Third Party Interference | FP:398683 Car v Pole Rreport manually created, Switching Schedule in attachments and restoration time acquired by meter data
|  | F-300001-I | Marua |  | Hikurangi CB1022 | 2025-11-27 22:33 | 45988.9398 | 2025-11-28 05:44 | 45989.2389 | 0.79885 | 0.010606 | 691 | 52048 | Unplanned | Defective Equipment | 398693/ Trip EF. Broken Xarm. Delay to attending fault due to ADMS upgrade cutover.
|  | F-300013-I | Pataua |  | Parua Bay CB1 | 2025-11-28 04:22 | 45989.182 | 2025-11-28 04:41 | 45989.1949 | 0.051094 | 0.014734 | 960 | 3329 | Unplanned | Unknown | Trip O/C Phase AB, Unknown. FPI activated Switch 988
|  | F-300019-I | Awakino Point |  | Dargaville CB4 | 2025-11-28 05:26 | 45989.2266 | 2025-11-28 05:42 | 45989.2373 | 0.088206 | 0.0057402 | 374 | 5747 | Unplanned | Unknown | Trip Unknown O/C Phase AB
|  | O-21133-A | Coast |  | Dargaville CB6 | 2025-11-28 08:32 | 45989.3554 | 2025-11-28 17:21 | 45989.7229 | 0.86113 | 0.0016269 | 106 | 56106 | Planned | Planned Interruption | Remove SW 2065 Install new SW 10269 remove Temp links @ pole 55186. Reconfigure 11KV. Run late due to work load.
|  | O-21214-A | Hakaru |  | Kaiwaka CB1032 | 2025-11-28 09:16 | 45989.3859 | 2025-11-28 13:29 | 45989.5617 | 0.41571 | 0.0016423 | 107 | 27085 | Planned | Planned Interruption | Replace conductors between Poles 913620 and 909855
|  | F-300001-H | Hakaru |  | Kaiwaka CB1032 | 2025-11-28 16:16 | 45989.678 | 2025-11-28 20:14 | 45989.8431 | 1.3527 | 0.026215 | 1708 | 88136 | Unplanned | Vegetation | FP398731 - Remove tree from lines
|  | O-21631-A | Port |  | Bream Bay CB1110 | 2025-11-30 09:01 | 45991.3757 | 2025-11-30 10:23 | 45991.4326 | 0.0025171 | 3.0697e-05 | 2 | 164 | Planned | Planned Interruption | Network Maintenance - Isolate and earth to check Clockwise or Antil Clockwise Rotation on 11kV
|  | F-300007-H | Golden Bay Sth |  | Maungatapere POS CB1382 | 2025-11-30 09:30 | 45991.3958 | [6 empty] | Unplanned | Unknown | 398739 - Tripped EF, Patrolled and livened, Unknown cause.
|  | F-300013-H | Marsden Bay |  | Bream Bay CB1107 | 2025-11-30 18:07 | 45991.7547 | 2025-11-30 19:03 | 45991.7937 | 0.43816 | 0.025923 | 1689 | 28548 | Unplanned | Vegetation | 398746 / Bamboo burning in lines at pole 53990.
|  | O-21556-A | Rewa Rewa Rd |  | Whangarei South CB1082 | 2025-12-01 08:46 | 45992.3652 | 2025-12-01 10:02 | 45992.4184 | 0.069371 | 0.0009063 | 59 | 4516 | Planned | Planned Interruption | Level foundation of TX
|  | O-21013-A | Waipu |  | Ruakaka CB2 | 2025-12-01 09:02 | 45992.3761 | 2025-12-01 14:24 | 45992.6003 | 0.52566 | 0.0016283 | 106 | 34220 | Planned | Planned Interruption | Replace poles 10223, 10224 & 10407
|  | O-21448-A | Maunu |  | Maunu CB1032 | 2025-12-01 11:41 | 45992.487 | 2025-12-01 14:24 | 45992.6003 | 0.13286 | 0.00081414 | 53 | 8649 | Planned | Planned Interruption | Level Tx S278
|  | F-300016-H | Tangowahine |  | Dargaville CB8 | 2025-12-01 13:50 | 45992.5764 | 2025-12-01 14:59 | 45992.6243 | 0.10917 | 0.0015822 | 103 | 7107 | Unplanned | Defective Equipment | 398764/ Broken guy wire (rusted in half, mid way)
|  | O-21217-A | Hakaru |  | Kaiwaka CB1032 | 2025-12-02 09:03 | 45993.377 | 2025-12-02 14:09 | 45993.5897 | 0.42824 | 0.0013979 | 91 | 27878 | Planned | Planned Interruption | Replacing overhead HV conductors
|  | O-21325-A | Te Kopuru |  | Dargaville CB2 | 2025-12-02 09:11 | 45993.3828 | 2025-12-02 13:09 | 45993.548 | 0.065776 | 0.0002765 | 18 | 4282 | Planned | Planned Interruption | Install new Tx L301
|  | O-21562-A | Poroti |  | Maungatapere CB2 | 2025-12-03 09:36 | 45994.4 | 2025-12-03 14:25 | 45994.6007 | 0.31519 | 0.0010906 | 71 | 20519 | Planned | Planned Interruption | Resag conductor
|  | O-21436-A | Taipuha |  | Mareretu CB1 | 2025-12-03 09:38 | 45994.4014 | 2025-12-03 10:51 | 45994.4521 | 0.019063 | 0.00026114 | 17 | 1241 | Planned | Planned Interruption | Replace pole
|  | F-300022-H | POR - WAI - MPEN |  | Maungatapere POS CB1312 | 2025-12-03 13:56 | 45994.5806 | 2025-12-03 14:57 | 45994.6229 | 0.81225 | 0.024624 | 1603 | 52877 | Unplanned | Vegetation | FP 398862 - Tree branch over 33kV line
|  | F-300025-H | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-12-03 14:17 | 45994.595 | 2025-12-03 14:32 | 45994.6054 | 0.11893 | 0.007911 | 515 | 7742 | Unplanned | Adverse Weather | Trip O/C, Phase ABC involved in Fault
|  | F-300034-H | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-12-03 14:50 | 45994.6181 | 2025-12-03 15:57 | 45994.6646 | 0.0092627 | 0.00013825 | 9 | 603 | Unplanned | Lightning | FP 398865 - Found 3x HV fuses blown.
|  | F-300040-H | North Kaiwaka |  | Kaiwaka CB1022 | 2025-12-03 16:06 | 45994.6708 | 2025-12-03 17:22 | 45994.7236 | 0.0046698 | 6.1444e-05 | 4 | 304 | Unplanned | Lightning | FP 398869 - found 3x HV fuses blown
|  | F-300046-H | North Kaiwaka |  | Kaiwaka CB1022 | 2025-12-03 17:51 | 45994.7438 | 2025-12-03 23:29 | 45994.9785 | 0.042735 | 0.00039939 | 26 | 2782 | Unplanned | Lightning | FP 398869 - Replaced HV Fuses & Tx
|  | F-300049-H | North Kaiwaka |  | Kaiwaka CB1022 | 2025-12-03 18:27 | 45994.7688 | 2025-12-03 18:45 | 45994.7812 | 0.0002765 | 1.5361e-05 | 1 | 18 | Unplanned | Lightning | HV Fuses found open after lightning - closed x3
|  | F-300055-H | Titoki |  | Poroti CB1032 | 2025-12-04 02:33 | 45995.1063 | 2025-12-04 04:30 | 45995.1875 | 0.40658 | 0.005146 | 335 | 26468 | Unplanned | Adverse Weather | FP 398877 - No fault found, Tripped ABC
|  | F-300064-H | Titoki |  | Poroti CB1032 | 2025-12-04 05:53 | 45995.2453 | 2025-12-04 09:30 | 45995.3958 | 0.0033334 | 1.5361e-05 | 1 | 217 | Unplanned | Vegetation | 398878/ x3 HV blown fuses. Branch blown onto jumpers between DDO's & Tx. Not initially noticed 3rd DDO was blown but not dropped
|  | F-300058-H | Tangowahine |  | Dargaville CB8 | 2025-12-04 06:02 | 45995.2517 | 2025-12-04 11:59 | 45995.4993 | 0.26546 | 0.0031337 | 204 | 17281 | Unplanned | Adverse Weather | FP 398879 - Recl 1504 A,B,C & E, sectionalised. Fed from Recl 1506 trip B & C. Returned to recl 1504 then tripped C & E onwards
|  | O-21124-A | Maungakaramea |  | Maungatapere CB3 | 2025-12-04 09:03 | 45995.3771 | 2025-12-04 14:55 | 45995.6215 | 0.35146 | 0.00099847 | 65 | 22880 | Planned | Planned Interruption | Pole changes and Pole hardware replacements
|  | O-21361-A | Taipuha |  | Mareretu CB1 | 2025-12-04 09:32 | 45995.3974 | 2025-12-04 12:31 | 45995.5212 | 0.11507 | 0.00064517 | 42 | 7491 | Planned | Planned Interruption | Replace pole
|  | F-300091-H | Jordan Valley |  | Hikurangi CB1102 | 2025-12-05 02:15 | 45996.094 | 2025-12-05 02:31 | 45996.1048 | 0.058557 | 0.0073733 | 480 | 3812 | Unplanned | Adverse Weather | Remotely restored
|  | O-21235-A | Hakaru |  | Kaiwaka CB1032 | 2025-12-05 09:01 | 45996.3757 | 2025-12-05 12:04 | 45996.5028 | 0.25581 | 0.0013979 | 91 | 16653 | Planned | Planned Interruption | Replacing overhead HV conductors
|  | O-21463-A | Okara Drive |  | Whangarei South CB1092 | 2025-12-05 09:18 | 45996.3875 | 2025-12-05 14:49 | 45996.6174 | 0.05593 | 0.00016897 | 11 | 3641 | Planned | Planned Interruption | Level foundation of TX
|  | F-300094-H | Springs Flat |  | Kamo CB1 | 2025-12-06 20:50 | 45997.8683 | 2025-12-06 21:05 | 45997.8787 | 0.052105 | 0.0081107 | 528 | 3392 | Unplanned | Unknown | SW 6021 A&B OC. Close <15min
|  | O-21184-A | Treatment |  | Kioreroa CB2 | 2025-12-07 09:03 | 45998.3771 | 2025-12-07 16:56 | 45998.7056 | 0.18848 | 0.00046083 | 30 | 12270 | Planned | Planned Interruption | Liven new Tx, remove Sw, rearrange feeder config
|  | O-21292-A | Kamo Town |  | Kamo CB7 | 2025-12-08 09:01 | 45999.3758 | 2025-12-08 15:56 | 45999.6641 | 0.61845 | 0.00149 | 97 | 40261 | Planned | Planned Interruption | Upgrade TX KK110 and replace poles
|  | O-21607-A | Bickerstaff |  | Maungaturoto CB2 | 2025-12-08 09:32 | 45999.3969 | 2025-12-08 13:11 | 45999.5496 | 0.28381 | 0.0012903 | 84 | 18476 | Planned | Planned Interruption | Network Maintenance - replace poles 16199 and 16200
|  | O-21358-A | Onoke |  | Kamo CB8 | 2025-12-08 09:36 | 45999.4 | 2025-12-08 13:56 | 45999.5806 | 0.18771 | 0.00072197 | 47 | 12220 | Planned | Planned Interruption | Tree Clearing Work
|  | O-21166-A | Austin Road |  | Maunu CB1072 | 2025-12-09 09:06 | 46000.3791 | 2025-12-09 13:01 | 46000.5424 | 0.039739 | 0.00016897 | 11 | 2587 | Planned | Planned Interruption | Upgrade Tx
|  | O-21439-A | Titoki |  | Poroti CB1032 | 2025-12-10 09:17 | 46001.3871 | 2025-12-10 15:08 | 46001.6307 | 0.032335 | 9.2167e-05 | 6 | 2105 | Planned | Planned Interruption | Replace poles, and hadware
|  | O-21478-A | MTON - MTO POS |  | Maungaturoto POS CB1262 | 2025-12-10 09:34 | 46001.3983 | 2025-12-10 14:39 | 46001.6104 | 0.056298 | 0.00018433 | 12 | 3665 | Planned | Planned Interruption | Replace Poles
|  | F-300106-H | Tangaihi |  | Ruawai CB1032 | 2025-12-10 09:50 | 46001.4095 | 2025-12-10 12:35 | 46001.5246 | 0.0076345 | 4.6083e-05 | 3 | 497 | Unplanned | Defective Equipment | FP 399034 - Shutdown to repair Broken HV jumper H376
|  | O-21181-A | Tangowahine |  | Dargaville CB8 | 2025-12-11 08:50 | 46002.3681 | 2025-12-11 15:49 | 46002.659 | 0.39905 | 0.00095239 | 62 | 25978 | Planned | Planned Interruption | repalce poles, hardwares, cross-arms and upgrade Tx
|  | O-21676-A | Waipu |  | Ruakaka CB2 | 2025-12-12 09:06 | 46003.3792 | 2025-12-12 14:10 | 46003.5903 | 0.56037 | 0.0018433 | 120 | 36480 | Planned | Planned Interruption | Tree Clearing Work
|  | O-21442-A | Coast |  | Dargaville CB6 | 2025-12-12 09:49 | 46003.409 | 2025-12-12 13:08 | 46003.5472 | 0.20699 | 0.001275 | 83 | 13475 | Planned | Planned Interruption | Replacing poles and hardware, 2 spans of LV under HV
|  | F-300133-H | Norfolk St |  | Alexander St CB1 | 2025-12-13 23:00 | 46004.9584 | 2025-12-14 02:36 | 46005.108 | 1.3585 | 0.033702 | 2194 | 88436 | Unplanned | Defective Equipment | 399146 - 2x Faults: 1st btwn SW 9319 & SW 282. 2nd btwn SW 283 & SW 161. Customers all back on.
|  | O-21691-A | Marsden Bay |  | Bream Bay CB1107 | 2025-12-14 20:35 | 46005.8574 | 2025-12-15 04:52 | 46006.203 | 0.43274 | 0.00087558 | 57 | 28171 | Planned | Planned Interruption | Repalce existing RMU with new CFCC
|  | O-21523-A | Charles St |  | Kamo CB2 | 2025-12-15 08:31 | 46006.3549 | 2025-12-15 10:10 | 46006.4236 | 0.10493 | 0.0010599 | 69 | 6831 | Planned | Planned Interruption | Fit neutral lugs flat
|  | O-21538-A | Puwera |  | Maungatapere CB7 | 2025-12-15 09:04 | 46006.3778 | 2025-12-15 13:40 | 46006.5694 | 0.61475 | 0.0022274 | 145 | 40020 | Planned | Planned Interruption | Network Maintenance HV POLE & HARDWARE REPLACEMENTS
|  | F-300139-H | Paparoa |  | Mareretu CB6 | 2025-12-15 15:08 | 46006.6306 | 2025-12-15 16:42 | 46006.696 | 0.078173 | 0.0008295 | 54 | 5089 | Unplanned | Defective Equipment | 399174 - HV pole Xarm brace bolt rusted off @ pole 21707
|  | O-21505-A | Tamaterau |  | Onerahi CB7 | 2025-12-16 09:01 | 46007.3757 | 2025-12-16 16:16 | 46007.6778 | 1.303 | 0.0029954 | 195 | 84825 | Planned | Planned Interruption | Network Maintenance - Xarm, conductor & Tx upgrades * Report needs updating *
|  | O-21466-A | Ararua |  | Mareretu CB2 | 2025-12-16 09:20 | 46007.3889 | 2025-12-16 11:36 | 46007.4833 | 0.060584 | 0.00044547 | 29 | 3944 | Planned | Planned Interruption | Replant and straighten pole
|  | F-300148-H | Tangowahine |  | Dargaville CB8 | 2025-12-16 15:36 | 46007.6501 | 2025-12-16 22:29 | 46007.937 | 0.16499 | 0.00039939 | 26 | 10741 | Unplanned | Defective Equipment | FP 399214 - Replaced cracked insulator
|  | F-300151-H | Jordan Valley |  | Hikurangi CB1102 | 2025-12-16 17:03 | 46007.7103 | 2025-12-16 19:30 | 46007.8125 | 0.16797 | 0.0073733 | 480 | 10935 | Unplanned | Defective Equipment | FP 399215 - HV pin insulator corroded
|  | F-300154-H | North Kaiwaka |  | Kaiwaka CB1022 | 2025-12-17 00:30 | 46008.021 | 2025-12-17 04:07 | 46008.1713 | 0.4445 | 0.004977 | 324 | 28937 | Unplanned | Vegetation | FP 399217 - Removed tree branch from lines near Pole 28319
|  | O-21577-A | Titoki |  | Poroti CB1032 | 2025-12-17 09:06 | 46008.3791 | 2025-12-17 12:13 | 46008.5089 | 0.14928 | 0.00079878 | 52 | 9718 | Planned | Planned Interruption | Replace, crossarms, hardware and conductor
|  | O-21232-A | Tangowahine |  | Dargaville CB8 | 2025-12-17 09:07 | 46008.3799 | 2025-12-17 16:53 | 46008.7034 | 0.21469 | 0.00046083 | 30 | 13976 | Planned | Planned Interruption | X-arm changes & associated maintenance.
|  | O-300199-H | Pataua |  | Parua Bay CB1 | 2025-12-17 09:31 | 46008.3964 | 2025-12-17 11:46 | 46008.4901 | 0.21971 | 0.0016283 | 106 | 14303 | Planned | Planned Interruption | Urgent Repairs- Replace rotten HV pin arm on pole 25206.
|  | O-21535-A | 2nd Ave |  | Alexander St CB3 | 2025-12-17 09:38 | 46008.4011 | 2025-12-17 11:11 | 46008.4661 | 0.045991 | 0.00049156 | 32 | 2994 | Planned | Planned Interruption | Level tx
|  | O-21529-A | Tamaterau |  | Onerahi CB7 | 2025-12-18 09:01 | 46009.376 | 2025-12-18 15:31 | 46009.6465 | 1.3165 | 0.0033794 | 220 | 85701 | Planned | Planned Interruption | Network Maintenance - Replacing 11kv 400v Poles Cross arms & Conductor.
|  | O-21616-A | Parua Bay |  | Parua Bay CB2 | 2025-12-18 09:34 | 46009.3986 | 2025-12-18 10:27 | 46009.4352 | 0.00081414 | 1.5361e-05 | 1 | 53 | Planned | Planned Interruption | Check high Partial Discharge at Tx 00554.
|  | O-21397-A | Titoki |  | Poroti CB1032 | 2025-12-18 09:41 | 46009.4033 | 2025-12-18 13:33 | 46009.5647 | 0.099985 | 0.00043011 | 28 | 6509 | Planned | Planned Interruption | Repair Oil leak HV termination
|  | O-300247-H | North Dargaville |  | Dargaville CB1 | 2025-12-18 10:09 | 46009.423 | 2025-12-18 13:42 | 46009.5706 | 0.029401 | 0.00013825 | 9 | 1914 | Planned | Planned Interruption | Replace crossarms and hardware
|  | O-300250-H | North Dargaville |  | Dargaville CB1 | 2025-12-18 10:29 | 46009.4368 | 2025-12-18 12:00 | 46009.5002 | 0.039217 | 0.00043011 | 28 | 2553 | Planned | Planned Interruption | Replace crossarm
|  | F-300157-H | Titoki |  | Poroti CB1032 | 2025-12-18 14:26 | 46009.6014 | 2025-12-18 14:46 | 46009.6153 | 0.00030722 | 1.5361e-05 | 1 | 20 | Unplanned | Human Error | FP 399260 Blown HV fuse - wrong sized fusing. Upgraded fuses x3.
|  | F-300163-H | Treatment |  | Kioreroa CB2 | 2025-12-18 21:29 | 46009.8951 | 2025-12-19 13:24 | 46010.5583 | 0.38142 | 0.00039939 | 26 | 24830 | Unplanned | Defective Equipment | FP 399270 - Repair UG cable fault
|  | O-1360-C | Titoki |  | Poroti CB1032 | 2025-12-19 09:01 | 46010.3758 | 2025-12-19 12:29 | 46010.5202 | 0.073441 | 0.00035331 | 23 | 4781 | Planned | Planned Interruption | Replace crossarms
|  | F-300166-H | Kaiatea |  | Ngunguru CB1072 | 2025-12-20 10:57 | 46011.4566 | 2025-12-20 10:59 | 46011.4573 | 0.011936 | 0.010538 | 686 | 777 | Unplanned | Unknown | FPI's 720 activated A & B phase Reports of sparks at pole 307343 - checked OK FP399294
|  | F-300172-H | Hakaru |  | Kaiwaka CB1032 | 2025-12-21 05:42 | 46012.2378 | 2025-12-21 05:58 | 46012.2485 | 0.07358 | 0.013057 | 850 | 4790 | Unplanned | Unknown | T & C >15min. A & B Ph OC
|  | F-300175-H | Jordan Valley |  | Hikurangi CB1102 | 2025-12-21 18:36 | 46012.775 | 2025-12-21 19:25 | 46012.809 | 0.0015054 | 3.0722e-05 | 2 | 98 | Unplanned | Wildlife | 399298 / Possum found on Tx HV Bushings.
|  | O-300349-H | Tangowahine |  | Dargaville CB8 | 2025-12-22 09:33 | 46013.398 | 2025-12-22 14:43 | 46013.6135 | 0.091767 | 0.001275 | 83 | 5974 | Planned | Planned Interruption | Tree Clearing Work
|  | F-300190-H | Three Mile Bush |  | Kamo CB3 | 2025-12-24 00:44 | 46015.0307 | 2025-12-24 01:39 | 46015.0689 | 0.027066 | 0.00049156 | 32 | 1762 | Unplanned | Wildlife | 399320 / Rat Vs HV Fuses. Replace HV fuses & BTN
|  | F-300193-H | Puwera |  | Maungatapere CB7 | 2025-12-25 10:28 | 46016.4358 | 2025-12-25 10:43 | 46016.4463 | 0.057082 | 0.007189 | 468 | 3716 | Unplanned | Unknown | Trip O/C B&C phase - 15 min close
|  | F-300199-H | KAI - MTO POS |  | Maungaturoto POS CB1222 | 2025-12-28 00:45 | 46019.0312 | 2025-12-28 01:02 | 46019.0433 | 1.7172 | 0.1061 | 6907 | 111790 | Unplanned | Unknown | FP 399372 - CB 1222 MTO tripped. Patrolled. Switching on F-300202-H
|  | F-300214-H | Wairere |  | Mareretu CB5 | 2025-12-28 22:54 | 46019.9543 | 2025-12-28 23:10 | 46019.9652 | 0.054993 | 0.0064517 | 420 | 3580 | Unplanned | Unknown | E/F - 15 min close
|  | F-300217-H | Ruatangata |  | Kamo CB6 | 2025-12-29 06:57 | 46020.2895 | 2025-12-29 07:13 | 46020.3009 | 0.1018 | 0.011521 | 750 | 6627 | Unplanned | Adverse Weather | B & C ph OC trip. Closed CB > 15mins
|  | F-300223-H | Ruatangata |  | Kamo CB6 | 2025-12-29 09:28 | 46020.3942 | 2025-12-29 15:51 | 46020.6604 | 0.78523 | 0.022642 | 1474 | 51118 | Unplanned | Vegetation | FP 399401 - Cleared trees from 11kV
|  | F-300226-H | Marua |  | Hikurangi CB1022 | 2025-12-29 09:47 | 46020.4079 | 2025-12-29 10:06 | 46020.4209 | 0.047128 | 0.0048695 | 317 | 3068 | Unplanned | Adverse Weather | A B ph OC - Closed > 15mins
|  | F-300229-H | Kiripaka Rd |  | Tikipunga CB8 | 2025-12-29 09:57 | 46020.4143 | 2025-12-29 19:07 | 46020.7964 | 3.1282 | 0.013088 | 852 | 203647 | Unplanned | Vegetation | 399396/ Tree in lines multiple locations
|  | F-300241-H | Tamaterau |  | Onerahi CB7 | 2025-12-29 10:35 | 46020.4406 | 2025-12-29 10:58 | 46020.457 | 0.18063 | 0.0082182 | 535 | 11759 | Unplanned | Adverse Weather | B & C OC - Closed > 15 mins (times had to be adjusted manually)
|  | F-300232-H | Bickerstaff |  | Maungaturoto CB2 | 2025-12-29 10:36 | 46020.4415 | 2025-12-29 10:59 | 46020.4577 | 0.19203 | 0.011843 | 771 | 12501 | Unplanned | Adverse Weather | Trip OC Phase AB - Portable FPI Flagged Pole 23503
|  | F-300235-H | Hotel |  | Poroti CB1052 | 2025-12-29 10:41 | 46020.445 | 2025-12-29 10:52 | 46020.453 | 0.050968 | 0.005361 | 349 | 3318 | Unplanned | Adverse Weather | Trip OC - FPI Sw 10349 Phase ABC
|  | F-300238-H | Whangarei Heads |  | Parua Bay CB3 | 2025-12-29 10:50 | 46020.4514 | 2025-12-29 11:06 | 46020.4627 | 0.19562 | 0.012274 | 799 | 12735 | Unplanned | Adverse Weather | Trip OC Phase B
|  | F-300244-H | Parua Bay |  | Parua Bay CB2 | 2025-12-29 10:54 | 46020.4542 | 2025-12-29 17:34 | 46020.7323 | 0.42896 | 0.0091245 | 992 | 28064 | Unplanned | Vegetation | 399404/ Lines Down (Tree branch came down).
|  | F-300250-H | Wairere |  | Mareretu CB5 | 2025-12-29 11:20 | 46020.4724 | 2025-12-29 12:09 | 46020.5065 | 0.21678 | 0.019601 | 1276 | 14112 | Unplanned | Adverse Weather | Trip OC Phase AB. (ICP's to be reviewed due to abnormal feeder config)
|  | F-300253-H | Poroti |  | Maungatapere CB2 | 2025-12-29 11:25 | 46020.4757 | 2025-12-29 11:47 | 46020.4906 | 0.091675 | 0.0096007 | 625 | 5968 | Unplanned | Adverse Weather | FPIs Sw8073 Phase ABC
|  | F-300265-H | Whangarei Heads |  | Parua Bay CB3 | 2025-12-29 11:29 | 46020.4787 | 2025-12-29 12:48 | 46020.5333 | 0.95938 | 0.012274 | 799 | 62455 | Unplanned | Adverse Weather | Trip Unknown. Faulty FPI's Sw 977
|  | F-300256-H | ToeToe Rd |  | Kioreroa CB7 | 2025-12-29 11:33 | 46020.4812 | 2025-12-29 11:59 | 46020.4992 | 0.097973 | 0.0094164 | 613 | 6378 | Unplanned | Adverse Weather | Trip - FPI Sw 10094 Phase BC & EF
|  | F-300259-H | Maungakaramea |  | Maungatapere CB3 | 2025-12-29 11:53 | 46020.4948 | 2025-12-29 12:49 | 46020.5339 | 0.22318 | 0.014132 | 920 | 14529 | Unplanned | Vegetation | 399424/ Vegetation over HV sagging with heavy rain
|  | F-300262-H | Commercial |  | Mangawhai Central CB1042 | 2025-12-29 12:01 | 46020.5008 | 2025-12-29 12:20 | 46020.5139 | 0.18636 | 0.01361 | 886 | 12132 | Unplanned | Adverse Weather | Trip OC Phase A&B
|  | F-300274-H | Kaiwaka Town |  | Kaiwaka CB1062 | 2025-12-29 12:10 | 46020.5069 | 2025-12-29 14:57 | 46020.6231 | 1.0792 | 0.0064824 | 422 | 70255 | Unplanned | Defective Equipment | Recl 1508 no comms.No power calls past recloser, when attended found open.Closed bypass SW. - PSU fail SW 333 @ 12.10 (Time off)
|  | F-300268-H | Hakaru |  | Kaiwaka CB1032 | 2025-12-29 12:24 | 46020.5163 | 2025-12-29 17:31 | 46020.7299 | 1.565 | 0.013164 | 857 | 101880 | Unplanned | Vegetation | 399423/ Trees in line
|  | F-300271-H | Bickerstaff |  | Maungaturoto CB2 | 2025-12-29 12:28 | 46020.5196 | 2025-12-30 00:08 | 46021.0056 | 1.3551 | 0.022228 | 1447 | 88219 | Unplanned | Vegetation | 399432/Lines down
|  | F-300277-H | North Kaiwaka |  | Kaiwaka CB1022 | 2025-12-29 12:54 | 46020.5373 | 2025-12-29 21:00 | 46020.8751 | 0.83813 | 0.0034409 | 224 | 54562 | Unplanned | Vegetation | 399458/Tree across Line/ Pole. Broken Xarm
|  | F-300280-H | Commercial |  | Mangawhai Central CB1042 | 2025-12-29 13:24 | 46020.5581 | 2025-12-29 13:50 | 46020.5762 | 0.21756 | 0.0084025 | 547 | 14163 | Unplanned | Adverse Weather | Trip OC Phase A&B.
|  | F-300283-H | Wairere |  | Mareretu CB5 | 2025-12-29 14:03 | 46020.5853 | 2025-12-29 14:21 | 46020.5977 | 0.11218 | 0.0064517 | 420 | 7303 | Unplanned | Adverse Weather | Trip OC Phase AB
|  | F-300298-H | Kaiwaka South |  | Kaiwaka CB1072 | 2025-12-29 20:40 | 46020.8614 | 2025-12-29 21:02 | 46020.8766 | 0.023165 | 0.0010599 | 69 | 1508 | Unplanned | Vegetation | 399456/ Branch on line
|  | F-300304-H | Coast |  | Dargaville CB6 | 2025-12-30 07:24 | 46021.3081 | 2025-12-30 16:10 | 46021.6738 | 0.36238 | 0.0027957 | 182 | 23591 | Unplanned | Defective Equipment | 399483 / Feeder fault caused by Faulty Tx L174. Replaced & BTN
|  | F-300307-H | Mata |  | Ruakaka CB3 | 2025-12-30 10:53 | 46021.4534 | 2025-12-30 11:29 | 46021.4781 | 0.080077 | 0.0068357 | 445 | 5213 | Unplanned | Adverse Weather | Sw 503 FPIs activated. High winds at the time. Closed & BTN.
|  | F-300313-H | Kokopu |  | Poroti CB1022 | 2025-12-30 14:15 | 46021.5938 | 2025-12-30 16:58 | 46021.7072 | 0.29369 | 0.0063134 | 411 | 19119 | Unplanned | Defective Equipment | 399503 / King bolt missing and conductor touching pole 31341. Repaired & btn
|  | F-300319-H | Chip Mill |  | Maungatapere POS CB1302 | 2025-12-30 20:03 | 46021.8353 | 2025-12-30 20:48 | 46021.8665 | 5.5673 | 0.1636 | 10650 | 362426 | Unplanned | Vegetation | 399514 - Lines down on 33kV to Chip Mill caused MPE GXP outage
|  | F-300322-H | Walton St |  | Whangarei South CB1022 | 2025-12-31 00:02 | 46022.0011 | 2025-12-31 12:19 | 46022.5132 | 2.1427 | 0.0087712 | 571 | 139486 | Unplanned | Third Party Interference | 399515 - Car Vs pole 341712 (Tx WC326 on pole)
|  | F-300325-H | Wairere |  | Mareretu CB5 | 2025-12-31 14:17 | 46022.5951 | 2025-12-31 14:48 | 46022.6165 | 0.12042 | 0.0064517 | 420 | 7839 | Unplanned | Unknown | Tripped O/C B&C phase - Sw 381 FPI's activated
|  | F-300334-H | Kiripaka Rd |  | Tikipunga CB8 | 2026-01-01 14:31 | 46023.6046 | 2026-01-01 14:33 | 46023.6061 | 0.040369 | 0.019693 | 1282 | 2628 | Unplanned | Third Party Interference | 399544 - Balloons in lines on Corks Rd Pole 40093, balloons all clear so closed feeder
|  | F-300346-H | Puwera |  | Maungatapere CB7 | 2026-01-02 17:21 | 46024.7231 | 2026-01-02 19:12 | 46024.8 | 0.0033948 | 3.0722e-05 | 2 | 221 | Unplanned | Lightning | 399556 - 3x HV fuses blown - Lightning
|  | F-300349-H | Maungakaramea |  | Maungatapere CB3 | 2026-01-02 21:22 | 46024.89 | 2026-01-02 21:42 | 46024.904 | 0.11656 | 0.0091859 | 598 | 7588 | Unplanned | Lightning | Tripped O/C A&B phase - Unknown, Lightning in area
|  | F-300352-H | Paparoa |  | Mareretu CB6 | 2026-01-03 00:45 | 46025.0309 | 2026-01-03 04:00 | 46025.1665 | 1.691 | 0.0091399 | 595 | 110083 | Unplanned | Vegetation | 399561 - Fire & tree on lines reported by Fire emergency
|  | F-300355-H | Whatatiri |  | Maungatapere CB8 | 2026-01-03 07:07 | 46025.2966 | 2026-01-03 13:30 | 46025.5622 | 0.8191 | 0.0058526 | 381 | 53323 | Unplanned | Defective Equipment | FP 399563. Broken preform - Line down pole 59769. Sw 849 FTO remotely - delayed backfeed. Traffic Management delays.
|  | F-300376-H | Tamaterau |  | Onerahi CB7 | 2026-01-03 13:46 | 46025.5736 | 2026-01-03 16:14 | 46025.6764 | 0.043195 | 0.00029186 | 19 | 2812 | Unplanned | Lightning | 399573 - 3x HV fuses blown - lightning
|  | F-300370-H | Whangarei Heads |  | Parua Bay CB3 | 2026-01-03 17:08 | 46025.7138 | 2026-01-03 18:25 | 46025.767 | 0.058879 | 0.00076806 | 50 | 3833 | Unplanned | Vegetation | 399580 - Clear trees burning in lines between poles 24340 & 24341
|  | F-300373-H | Brynderwyn |  | Maungaturoto CB1 | 2026-01-03 17:45 | 46025.7396 | 2026-01-03 21:50 | 46025.9097 | 0.14579 | 0.00066053 | 43 | 9491 | Unplanned | Lightning | 399581 - Found blown HV jumper at Sw 6082, switch faulty & needs replacing, switch bypassed - Lightning
|  | F-300391-H | Tangowahine |  | Dargaville CB8 | 2026-01-04 21:25 | 46026.892 | 2026-01-04 21:40 | 46026.9028 | 0.034086 | 0.003149 | 205 | 2219 | Unplanned | Unknown | 15 min close
|  | O-300025-H | Te Kopuru |  | Dargaville CB2 | 2026-01-05 09:36 | 46027.4 | 2026-01-05 13:39 | 46027.5687 | 0.029862 | 0.00012289 | 8 | 1944 | Planned | Planned Interruption | Replace crossarm and HV connections
|  | F-300409-H | Mata |  | Ruakaka CB3 | 2026-01-06 06:41 | 46028.2788 | 2026-01-06 12:23 | 46028.5163 | 0.69999 | 0.0068357 | 445 | 45569 | Unplanned | Defective Equipment | 399630 / 1 x HV line down between Pole 22593 & Sw 500. No Cause Found.
|  | O-300082-H | Jordan Valley |  | Hikurangi CB1102 | 2026-01-06 09:03 | 46028.3771 | 2026-01-06 12:29 | 46028.5201 | 0.10126 | 0.00049156 | 32 | 6592 | Planned | Planned Interruption | Replace Pole and TX
|  | O-300232-H | Tangowahine |  | Dargaville CB8 | 2026-01-06 09:09 | 46028.3811 | 2026-01-06 14:06 | 46028.5872 | 0.12369 | 0.000553 | 36 | 8052 | Planned | Planned Interruption | Replace pole 36855 & remove temp break @ Pole 36858
|  | O-300175-H | Bickerstaff |  | Maungaturoto CB2 | 2026-01-06 09:14 | 46028.3847 | 2026-01-06 13:43 | 46028.5715 | 0.13636 | 0.00050692 | 33 | 8877 | Planned | Planned Interruption | Replace crossarms, hardware and HV links
|  | O-21619-A | Tangowahine |  | Dargaville CB8 | 2026-01-07 09:05 | 46029.3785 | 2026-01-07 12:29 | 46029.5201 | 0.12848 | 0.00062981 | 41 | 8364 | Planned | Planned Interruption | Replace pole hardware and crossarms
|  | O-300205-H | Bickerstaff |  | Maungaturoto CB2 | 2026-01-07 09:09 | 46029.3812 | 2026-01-07 14:10 | 46029.5903 | 0.10172 | 0.00033794 | 22 | 6622 | Planned | Planned Interruption | Straighten Poles
|  | O-21433-A | Ararua |  | Mareretu CB2 | 2026-01-07 09:14 | 46029.3847 | 2026-01-07 12:48 | 46029.5333 | 0.0098618 | 4.6083e-05 | 3 | 642 | Planned | Planned Interruption | Upgrade TX E274 to 3ph 50kva and replace pole hardware
|  | O-300172-H | King Road |  | Mangawhai North CB2 | 2026-01-08 09:40 | 46030.4028 | 2026-01-08 15:45 | 46030.6562 | 0.056068 | 0.00015361 | 10 | 3650 | Planned | Planned Interruption | Upgrade Tx MC274
|  | O-300208-H | Austin Road |  | Maunu CB1072 | 2026-01-08 09:44 | 46030.4056 | 2026-01-08 15:00 | 46030.625 | 0.043687 | 0.00013825 | 9 | 2844 | Planned | Planned Interruption | Transformer Upgrade of S209
|  | F-300436-H | Te Kopuru |  | Dargaville CB2 | 2026-01-08 16:25 | 46030.684 | 2026-01-08 17:29 | 46030.7285 | 0.02851 | 0.00044547 | 29 | 1856 | Unplanned | Defective Equipment | FP 399724 - Repair broken deadend
|  | O-300214-H | Langs Beach |  | Mangawhai North CB3 | 2026-01-09 09:02 | 46031.3761 | 2026-01-09 11:37 | 46031.4842 | 0.019125 | 0.00012289 | 8 | 1245 | Planned | Planned Interruption | Replace HV links & hardware
|  | O-300445-H | Coast |  | Dargaville CB6 | 2026-01-09 09:31 | 46031.3966 | 2026-01-09 12:26 | 46031.5181 | 0.080108 | 0.00067589 | 44 | 5215 | Planned | Planned Interruption | Install temp breaks to accomdate 66kV line build
|  | F-300451-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-01-10 12:44 | 46032.5308 | 2026-01-10 15:23 | 46032.6412 | 0.21238 | 0.0013364 | 87 | 13826 | Unplanned | Third Party Interference | FP 399758 - FENZ F4375127 Car vs pole
|  | F-300454-H | Tamaterau |  | Onerahi CB7 | 2026-01-10 14:39 | 46032.6104 | 2026-01-11 01:57 | 46033.0809 | 0.69206 | 0.013625 | 887 | 45053 | Unplanned | Third Party Interference | FP399761 - Car vs Pole - F4375303. Temp Break installed pole 51628 to replace pole 410442
|  | F-300460-H | Whau Valley |  | Tikipunga CB1 | 2026-01-11 13:04 | 46033.5444 | 2026-01-11 22:25 | 46033.934 | 0.35332 | 0.00062981 | 41 | 23001 | Unplanned | Defective Equipment | FP399765 - report of fire on pole - FENZ 4375829. Cable crutch burnt out WC 146
|  | F-300463-H | Wairere |  | Mareretu CB5 | 2026-01-12 04:00 | 46034.1664 | 2026-01-12 04:15 | 46034.1772 | 0.052612 | 0.0064517 | 420 | 3425 | Unplanned | Unknown | A & B ph OC. Close > 15min
|  | O-300265-H | Ararua |  | Mareretu CB2 | 2026-01-12 09:05 | 46034.3785 | 2026-01-12 14:03 | 46034.5854 | 0.18768 | 0.00062981 | 41 | 12218 | Planned | Planned Interruption | Replace 11kV arms and connections, Upgrade Tx Y123 from 10kVA to 30kVA
|  | O-21625-A | Swamp North |  | Hikurangi CB1042 | 2026-01-12 09:52 | 46034.4111 | 2026-01-12 13:02 | 46034.5431 | 0.023349 | 0.00012289 | 8 | 1520 | Planned | Planned Interruption | Replace poles and crossarms
|  | F-300466-H | Maunu Road |  | Whangarei South CB1102 | 2026-01-12 16:44 | 46034.697 | 2026-01-12 17:10 | 46034.7152 | 0.16089 | 0.01447 | 942 | 10474 | Unplanned | Wildlife | FP 399797 Possum on line at pole 40633 Murdoch Cres
|  | F-300472-H | North River |  | Ruakaka CB7 | 2026-01-13 05:43 | 46035.2383 | 2026-01-13 06:32 | 46035.272 | 0.47248 | 0.017512 | 1140 | 30758 | Unplanned | Wildlife | FP 399802 - Swan strike pole 40891
|  | O-300427-H | Ararua |  | Mareretu CB2 | 2026-01-13 09:01 | 46035.3758 | 2026-01-13 13:41 | 46035.5702 | 0.64517 | 0.0023042 | 150 | 42000 | Planned | Planned Interruption | Install new Tx A173
|  | O-1381-C | Titoki |  | Poroti CB1032 | 2026-01-13 09:02 | 46035.3762 | 2026-01-13 14:15 | 46035.5935 | 0.062489 | 0.00019969 | 13 | 4068 | Planned | Planned Interruption | Replace pole
|  | O-300034-H | Austin Road |  | Maunu CB1072 | 2026-01-13 09:05 | 46035.3785 | 2026-01-13 14:17 | 46035.5951 | 0.47447 | 0.0015207 | 99 | 30888 | Planned | Planned Interruption | Install new Tx S312 and remove Tx S146
|  | F-300484-H | Marsden South |  | Bream Bay CB1111 | 2026-01-13 21:01 | 46035.8759 | 2026-01-13 22:25 | 46035.934 | 0.11805 | 0.0015668 | 102 | 7685 | Unplanned | Unknown | FP 399829 - Patrolled & livened
|  | O-300037-H | Titoki |  | Poroti CB1032 | 2026-01-14 09:06 | 46036.3791 | 2026-01-14 12:06 | 46036.5044 | 0.11638 | 0.00064517 | 42 | 7576 | Planned | Planned Interruption | Replace Poles
|  | O-21238-A | Tangowahine |  | Dargaville CB8 | 2026-01-14 09:18 | 46036.3875 | 2026-01-14 14:04 | 46036.5861 | 0.16255 | 0.00056836 | 37 | 10582 | Planned | Planned Interruption | X-arm & pole changes
|  | O-300328-H | Tamaterau |  | Onerahi CB7 | 2026-01-14 09:38 | 46036.4014 | 2026-01-14 12:43 | 46036.5299 | 0.26145 | 0.0014132 | 92 | 17020 | Planned | Planned Interruption | Replace hot stick connectors
|  | O-300289-H | Ararua |  | Mareretu CB2 | 2026-01-14 10:02 | 46036.4181 | 2026-01-14 10:31 | 46036.4382 | 0.0017819 | 6.1444e-05 | 4 | 116 | Planned | Planned Interruption | Redo connection on Pole 300319
|  | O-300094-H | Turiwiri |  | Dargaville CB9 | 2026-01-15 09:03 | 46037.3771 | 2026-01-15 09:45 | 46037.4062 | 0.011613 | 0.0002765 | 18 | 756 | Planned | Planned Interruption | Remove spur line and Tx J245
|  | O-300136-H | Paranui |  | Tikipunga CB6 | 2026-01-15 09:04 | 46037.3778 | 2026-01-15 17:29 | 46037.7285 | 0.14737 | 0.00029186 | 19 | 9594 | Planned | Planned Interruption | Replace RMU. Ran over time due to work load.
|  | O-300085-H | Tangowahine |  | Dargaville CB8 | 2026-01-15 09:06 | 46037.3792 | 2026-01-15 14:05 | 46037.5868 | 0.055116 | 0.00018433 | 12 | 3588 | Planned | Planned Interruption | Crossarm changes
|  | O-300490-H | Titoki |  | Poroti CB1032 | 2026-01-15 09:11 | 46037.3826 | 2026-01-15 15:39 | 46037.6521 | 1.3589 | 0.0035023 | 228 | 88464 | Planned | Planned Interruption | Replace poles. Ran a little over time due to work load.
|  | O-300448-H | Kokopu |  | Poroti CB1022 | 2026-01-15 09:37 | 46037.4007 | 2026-01-15 12:03 | 46037.5021 | 0.09868 | 0.00067589 | 44 | 6424 | Planned | Planned Interruption | Replace pole
|  | F-300511-H | 2nd Ave |  | Alexander St CB3 | 2026-01-15 23:27 | 46037.9772 | 2026-01-16 00:02 | 46038.0015 | 0.3661 | 0.017051 | 1110 | 23833 | Unplanned | Wildlife | FP 399892 Possum
|  | O-300229-H | Puwera |  | Maungatapere CB7 | 2026-01-16 09:07 | 46038.3799 | 2026-01-16 15:26 | 46038.6431 | 0.21541 | 0.00056836 | 37 | 14023 | Planned | Planned Interruption | HV ARM & HARDWARE REPLACEMENTS - pole 46907 to EOL
|  | O-300430-H | Dunns Rd |  | Ruawai CB1082 | 2026-01-16 09:08 | 46038.3806 | 2026-01-16 11:25 | 46038.4757 | 0.10733 | 0.00078342 | 51 | 6987 | Planned | Planned Interruption | Repalce Pole
|  | O-300226-H | Tikipunga Hill |  | Tikipunga CB4 | 2026-01-16 09:10 | 46038.382 | 2026-01-16 16:17 | 46038.6788 | 0.53836 | 0.0012596 | 82 | 35047 | Planned | Planned Interruption | Replace 11kV pothead and cable riser - Late restoration, large scope of works, additional AP's & Test permits added to switching
|  | F-300517-H | Taipuha |  | Mareretu CB1 | 2026-01-17 04:18 | 46039.1795 | 2026-01-17 04:20 | 46039.1804 | 0.0095546 | 0.0070815 | 461 | 622 | Unplanned | Unknown | Trip Overcurrent Phase B/C
|  | O-300295-H | Port Feeder |  | Bream Bay CB1110 | 2026-01-17 05:23 | 46039.2244 | 2026-01-18 10:56 | 46040.4553 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | Replacement of Northport Sub 1 - 11kv Breaker
|  | F-300529-H | Otangarei |  | Tikipunga CB7 | 2026-01-17 23:46 | 46039.9904 | 2026-01-18 01:53 | 46040.0785 | 1.0229 | 0.01573 | 1024 | 66592 | Unplanned | Defective Equipment | 399920 / LA fault causing feeder fault & tripped KEN-KMO Feeder 2 line. No Lightning in the area at the time.
|  | F-300532-H | Tikipunga Hill |  | Tikipunga CB4 | 2026-01-18 01:52 | 46040.0777 | 2026-01-18 02:08 | 46040.0886 | 0.11263 | 0.0072044 | 469 | 7332 | Unplanned | Lightning | Lightning in area. Most probable cause
|  | F-300538-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 03:52 | 46040.161 | 2026-01-18 04:07 | 46040.1717 | 0.25796 | 0.016805 | 1094 | 16793 | Unplanned | Lightning | Lightning. 15 min close & BTN
|  | F-300541-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 05:15 | 46040.219 | 2026-01-19 01:30 | 46041.0626 | 4.4845 | 0.017957 | 1169 | 291939 | Unplanned | Vegetation | 399924 - HV lines down due to tree at pole 302798, also slip reported past Links 6033. Lost power to Recl @ 06.46 until 17.13hrs
|  | F-300547-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 05:31 | 46040.23 | 2026-01-18 05:49 | 46040.2424 | 0.19443 | 0.012289 | 800 | 12657 | Unplanned | Adverse Weather | Trip B & C Overcurrent. No Lightning at the time. Recl 1549 was off @ time of triipping.
|  | F-300553-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 06:46 | 46040.2819 | 2026-01-27 16:46 | 46049.6986 | 5.6187 | 0.035115 | 2286 | 365775 | Unplanned | Adverse Weather | FP 399950 - Broken Poles - Slip caused trees to come into lines. Reinstated Breaks once land stabilised - 27/1 F-300664
|  | F-300568-H | Otonga |  | Hikurangi CB1032 | 2026-01-18 08:04 | 46040.3361 | 2026-01-18 10:56 | 46040.4556 | 0.0026421 | 1.5361e-05 | 1 | 172 | Unplanned | Lightning | FP 399929 - Found 2 HV fuses blown, reload and close.
|  | F-300580-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 11:00 | 46040.458 | 2026-01-18 13:56 | 46040.5806 | 0.0027036 | 1.5361e-05 | 1 | 176 | Unplanned | Lightning | FP 399939 - Replaced blown HV fuses. Tested all ok
|  | F-300583-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 14:38 | 46040.6101 | 2026-01-18 21:39 | 46040.9021 | 0.012919 | 3.0722e-05 | 2 | 841 | Unplanned | Lightning | 399944 - 3x HV fuses blown, closed in and holding - lightning
|  | F-300589-H | Whakapara |  | Hikurangi CB1112 | 2026-01-18 18:11 | 46040.7575 | 2026-01-18 20:37 | 46040.859 | 0.0044854 | 3.0722e-05 | 2 | 292 | Unplanned | Lightning | 399951 - Found 3x HV fuses blown, closed in and holding - lightning
|  | O-300133-H | Tangowahine |  | Dargaville CB8 | 2026-01-19 09:30 | 46041.3955 | 2026-01-19 15:06 | 46041.6294 | 0.18625 | 0.000553 | 36 | 12125 | Planned | Planned Interruption | Replace pole and crossarms
|  | O-300115-H | Town Hikurangi |  | Hikurangi CB1082 | 2026-01-19 09:36 | 46041.3999 | 2026-01-19 12:12 | 46041.5081 | 0.093303 | 0.00059908 | 39 | 6074 | Planned | Planned Interruption | Bolt down transformer
|  | F-300601-H | Marsden South |  | Bream Bay CB1111 | 2026-01-19 21:21 | 46041.8893 | 2026-01-19 21:36 | 46041.8999 | 0.024025 | 0.0015668 | 102 | 1564 | Unplanned | Adverse Weather | OC B&C phase, Unknown, closed after 15mins (F4)
|  | F-300595-H | Whatatiri |  | Maungatapere CB8 | 2026-01-19 22:26 | 46041.9347 | 2026-01-20 00:45 | 46042.0312 | 0.023487 | 0.00016897 | 11 | 1529 | Unplanned | Defective Equipment | 399989 - Faulty HV UG cable lug at Links 8014
|  | F-300604-H | Bickerstaff |  | Maungaturoto CB2 | 2026-01-20 01:05 | 46042.0451 | 2026-01-20 12:28 | 46042.5194 | 0.50355 | 0.021244 | 1383 | 32781 | Unplanned | Vegetation | FP 399992 Trees through lines - Lines down
|  | F-300607-H | Tangowahine |  | Dargaville CB8 | 2026-01-20 04:50 | 46042.2012 | 2026-01-20 05:05 | 46042.2115 | 0.029724 | 0.0031337 | 204 | 1935 | Unplanned | Adverse Weather | O/C B&C phase, Unknown, closed after 15mins
|  | F-300610-H | Wairere |  | Mareretu CB5 | 2026-01-20 06:37 | 46042.2757 | 2026-01-20 12:00 | 46042.5 | 0.78844 | 0.0064517 | 596 | 51456 | Unplanned | Defective Equipment | FP 399994 11KV line down
|  | F-300613-H | Tangowahine |  | Dargaville CB8 | 2026-01-20 10:47 | 46042.4495 | 2026-01-20 11:59 | 46042.4994 | 0.11063 | 0.0031337 | 204 | 7202 | Unplanned | Vegetation | FP 400005 branch over line
|  | F-300616-H | Hakaru |  | Kaiwaka CB1032 | 2026-01-20 11:45 | 46042.4899 | 2026-01-20 16:31 | 46042.6882 | 1.5296 | 0.013042 | 849 | 99573 | Unplanned | Vegetation | FP 400011. Tree branch on line
|  | F-300634-H | Matapouri |  | Ngunguru CB1032 | 2026-01-21 04:06 | 46043.1709 | 2026-01-21 04:21 | 46043.1816 | 0.090385 | 0.012304 | 801 | 5884 | Unplanned | Adverse Weather | B C Ef trip - Closed >15mins. No FPIS SW 721
|  | O-300139-H | Titoki |  | Poroti CB1032 | 2026-01-21 09:08 | 46043.3806 | 2026-01-21 13:05 | 46043.5451 | 0.16383 | 0.00069125 | 45 | 10665 | Planned | Planned Interruption | Replace Poles
|  | F-300553-H | Whakapara |  | Hikurangi CB1112 | 2026-01-21 14:44 | 46043.6138 | 2026-01-21 16:17 | 46043.6783 | 0.38218 | 0.016744 | 1090 | 24880 | Unplanned | Adverse Weather | AB O.C - Livened in stages. Recl 1549 didnt operate.
|  | F-300649-H | Poroti |  | Maungatapere CB2 | 2026-01-21 15:46 | 46043.6567 | 2026-01-21 19:32 | 46043.8136 | 0.41355 | 0.0096007 | 625 | 26922 | Unplanned | Third Party Interference | FP 400039 - Car vs Pole
|  | F-300655-H | Otonga |  | Hikurangi CB1032 | 2026-01-21 17:49 | 46043.7422 | 2026-01-23 17:50 | 46045.7431 | 4.2254 | 0.005699 | 371 | 275073 | Unplanned | Adverse Weather | 400041 / Pole 57611 part of land slip. Temp break installed at pole 57610 & removed again. Line BTN
|  | F-300667-H | North River |  | Ruakaka CB7 | 2026-01-22 04:03 | 46044.1686 | 2026-01-22 05:37 | 46044.234 | 0.16959 | 0.0041629 | 271 | 11040 | Unplanned | Vegetation | FP 400045 - A, B & Ef. Customer reported veg caused trippings, lines were tangled but cleared. Had field staff check - All ok.
|  | F-300670-H | Matapouri |  | Ngunguru CB1032 | 2026-01-22 04:24 | 46044.1835 | 2026-01-22 04:40 | 46044.1941 | 0.083749 | 0.012304 | 801 | 5452 | Unplanned | Adverse Weather | A B O/C. Close >15min
|  | F-300673-H | ToeToe Rd |  | Kioreroa CB7 | 2026-01-22 07:31 | 46044.3129 | 2026-01-22 07:47 | 46044.3244 | 0.10114 | 0.0060984 | 397 | 6584 | Unplanned | Vegetation | 400048 / Tree fallen on LV lines causing low lines. De energise for safety till faultman can isolate LV.
|  | O-300340-H | Maungakaramea |  | Maungatapere CB3 | 2026-01-22 09:16 | 46044.3861 | 2026-01-22 15:07 | 46044.6299 | 0.026959 | 7.6806e-05 | 5 | 1755 | Planned | Planned Interruption | replace poles & hardware
|  | F-300652-H | Ararua |  | Mareretu CB2 | 2026-01-22 12:48 | 46044.5333 | 2026-01-22 14:37 | 46044.609 | 0.251 | 0.0023042 | 150 | 16340 | Unplanned | Third Party Interference | FP 400036 - Car V Pole. Replace pole 76017
|  | F-300685-H | Puwera |  | Maungatapere CB7 | 2026-01-22 19:51 | 46044.8271 | 2026-01-22 21:10 | 46044.8819 | 0.021843 | 0.0002765 | 18 | 1422 | Unplanned | Defective Equipment | Replaced crossarm FP400072
|  | F-300691-H | Ararua |  | Mareretu CB2 | 2026-01-24 05:50 | 46046.2432 | 2026-01-24 10:44 | 46046.4472 | 0.93045 | 0.036114 | 2351 | 60572 | Unplanned | Vegetation | 400133 - Tree in lines, HV lines down on double curcuit between poles 21622 & 21623
|  | F-300694-H | Kaiwaka Town |  | Kaiwaka CB1062 | 2026-01-24 10:04 | 46046.4195 | 2026-01-24 10:20 | 46046.4302 | 0.1218 | 0.0079263 | 516 | 7929 | Unplanned | Adverse Weather | O/C B&C phase - 15min close - high winds
|  | F-300697-H | Matapouri |  | Ngunguru CB1032 | 2026-01-24 13:47 | 46046.574 | 2026-01-24 14:02 | 46046.5846 | 0.097927 | 0.012304 | 801 | 6375 | Unplanned | Adverse Weather | O/C A&B phase - Closed in after 15mins F4 - high winds
|  | F-300706-H | Brynderwyn |  | Maungaturoto CB1 | 2026-01-25 21:27 | 46047.8938 | 2026-01-25 21:44 | 46047.9052 | 0.047696 | 0.0028879 | 188 | 3105 | Unplanned | Unknown | Overcurrent A B & C. 15 min close successful. Seen on 33kV so large fault current potentially close to substation.
|  | F-300709-H | Whau Valley |  | Tikipunga CB1 | 2026-01-26 05:21 | 46048.2231 | 2026-01-26 08:11 | 46048.3409 | 0.88091 | 0.0051921 | 338 | 57347 | Unplanned | Third Party Interference | FP 400154 Car vs pole
|  | O-300130-H | Tangowahine |  | Dargaville CB8 | 2026-01-27 09:05 | 46049.3786 | 2026-01-27 11:11 | 46049.4659 | 0.10624 | 0.00084486 | 55 | 6916 | Planned | Planned Interruption | X-Arm & Hardware changes on Poles 37086 & 37096.
|  | F-300712-H | Kaiatea |  | Ngunguru CB1072 | 2026-01-27 18:40 | 46049.7776 | 2026-01-27 23:10 | 46049.9653 | 1.1185 | 0.010522 | 685 | 72816 | Unplanned | Third Party Interference | 400201 - Car vs pole 342872
|  | O-300592-H | Titoki |  | Poroti CB1032 | 2026-01-28 09:05 | 46050.3785 | 2026-01-28 10:07 | 46050.4215 | 0.0028572 | 4.6083e-05 | 3 | 186 | Planned | Planned Interruption | Replace Tx W301 - Job cancelled due to truck fault. Tx not changed
|  | O-300142-H | Springs Flat |  | Kamo CB1 | 2026-01-28 09:08 | 46050.3806 | 2026-01-28 13:15 | 46050.5521 | 0.36424 | 0.0014747 | 96 | 23712 | Planned | Planned Interruption | Replace Poles
|  | O-300241-H | Otonga |  | Hikurangi CB1032 | 2026-01-28 09:16 | 46050.3861 | 2026-01-28 13:00 | 46050.5417 | 0.35441 | 0.0015822 | 103 | 23072 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | F-300718-H | Taipuha |  | Mareretu CB1 | 2026-01-28 14:14 | 46050.5931 | 2026-01-28 14:47 | 46050.6157 | 0.037496 | 0.0011521 | 75 | 2441 | Unplanned | Defective Equipment | FP-400220 Repaired jumper
|  | O-300145-H | Cairnfield Rd |  | Tikipunga CB5 | 2026-01-29 09:01 | 46051.3757 | 2026-01-29 16:21 | 46051.6813 | 0.43933 | 0.00099847 | 65 | 28600 | Planned | Planned Interruption | Replace Tx and pole hardware - ran late
|  | O-21331-A | Paranui |  | Tikipunga CB6 | 2026-01-29 09:05 | 46051.3785 | 2026-01-29 15:10 | 46051.6319 | 0.38687 | 0.0010599 | 69 | 25185 | Planned | Planned Interruption | Replace Poles and hardware
|  | O-300460-H | Taipuha |  | Mareretu CB1 | 2026-01-29 09:33 | 46051.3979 | 2026-01-29 12:51 | 46051.5354 | 0.10037 | 0.00050692 | 33 | 6534 | Planned | Planned Interruption | Replace Poles
|  | O-300397-H | Titoki |  | Poroti CB1032 | 2026-01-30 09:01 | 46052.376 | 2026-01-30 15:36 | 46052.65 | 0.054547 | 0.00013825 | 9 | 3551 | Planned | Planned Interruption | Replace poles and upgrade Tx
|  | O-300601-H | Tangowahine |  | Dargaville CB8 | 2026-01-30 09:11 | 46052.3826 | 2026-01-30 13:45 | 46052.5729 | 0.12627 | 0.00046083 | 30 | 8220 | Planned | Planned Interruption | Repalce X-arms and replant pole
|  | O-300598-H | Coast |  | Dargaville CB6 | 2026-02-02 09:31 | 46055.3965 | 2026-02-02 12:46 | 46055.5323 | 0.087082 | 0.00044547 | 29 | 5669 | Planned | Planned Interruption | Relocate Pole 63762
|  | F-300736-H | Pataua |  | Parua Bay CB1 | 2026-02-02 11:59 | 46055.4993 | 2026-02-02 14:16 | 46055.5946 | 0.12009 | 0.00087558 | 57 | 7818 | Unplanned | Defective Equipment | 400331 - Broken HV Xarm at pole 25707 & replaced DDO's PO134
|  | O-300274-H | Maungakaramea |  | Maungatapere CB3 | 2026-02-03 09:03 | 46056.3771 | 2026-02-03 13:12 | 46056.55 | 0.89885 | 0.0036099 | 235 | 58515 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | F-300745-H | Marsden Bay |  | Bream Bay CB1107 | 2026-02-04 07:14 | 46057.3016 | 2026-02-04 09:34 | 46057.3986 | 0.52881 | 0.0039785 | 259 | 34425 | Unplanned | Wildlife | FP 400420 - Dead bird found beside Pole 13474 with signs of coming into contact with O/H lines.
|  | O-300442-H | Tangowahine |  | Dargaville CB8 | 2026-02-04 09:04 | 46057.3778 | 2026-02-04 14:32 | 46057.6056 | 0.78415 | 0.0024117 | 157 | 51048 | Planned | Planned Interruption | Replace crossarms and hardware
|  | O-300469-H | Maungakaramea |  | Maungatapere CB3 | 2026-02-05 09:01 | 46058.3757 | 2026-02-05 14:11 | 46058.591 | 0.15714 | 0.00050692 | 33 | 10230 | Planned | Planned Interruption | Replace poles, crossarms, hardware
|  | F-300751-H | Charles St |  | Kamo CB2 | 2026-02-05 13:12 | 46058.5502 | 2026-02-05 18:25 | 46058.7673 | 0.82692 | 0.01682 | 1095 | 53832 | Unplanned | Third Party Interference | Hiab vs 11KV & 33KV repair burnt line - Delay due to incorrect sleeves for the 33KV FP 400476
|  | F-300769-H | Marsden South |  | Bream Bay CB1111 | 2026-02-08 07:10 | 46061.2988 | 2026-02-08 07:26 | 46061.3095 | 0.024071 | 0.0015668 | 102 | 1567 | Unplanned | Unknown | Trip B & C Phase O/C. 15 min close & BTN
|  | F-300772-H | Kiripaka Rd |  | Tikipunga CB8 | 2026-02-08 09:42 | 46061.4041 | 2026-02-08 09:59 | 46061.4163 | 0.22903 | 0.013088 | 852 | 14910 | Unplanned | Third Party Interference | 400492 / Branch vs lines causing trip. No damage to lines & re livened BTN
|  | O-301111-H | Town Dargaville |  | Dargaville CB3 | 2026-02-09 10:09 | 46062.4229 | 2026-02-09 16:46 | 46062.6986 | 0.024393 | 6.1444e-05 | 4 | 1588 | Planned | Planned Interruption | Replace Pole 32702 & maintenance on Pole 305642. Went over due to late start.
|  | O-300463-H | Swamp North |  | Hikurangi CB1042 | 2026-02-10 09:06 | 46063.3792 | 2026-02-10 15:18 | 46063.6375 | 0.27429 | 0.00073733 | 48 | 17856 | Planned | Planned Interruption | Replace pole
|  | O-300835-H | Paparoa |  | Mareretu CB6 | 2026-02-10 09:20 | 46063.3889 | 2026-02-10 16:10 | 46063.6736 | 1.4782 | 0.0036867 | 240 | 96233 | Planned | Planned Interruption | Network Renewal - Replace pole & crossarms. Ran overtime due to work load.
|  | O-300292-H | Tangowahine |  | Dargaville CB8 | 2026-02-11 09:12 | 46064.3836 | 2026-02-11 13:54 | 46064.5791 | 0.017297 | 6.1444e-05 | 4 | 1126 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | O-300904-H | Ruatangata |  | Kamo CB6 | 2026-02-11 09:17 | 46064.387 | 2026-02-11 14:38 | 46064.6095 | 0.33481 | 0.0010446 | 68 | 21796 | Planned | Planned Interruption | Install & Liven new Tx
|  | F-300793-H | Ruatangata |  | Kamo CB6 | 2026-02-11 10:38 | 46064.4431 | 2026-02-11 11:54 | 46064.4958 | 0.043195 | 0.00056836 | 37 | 2812 | Unplanned | Defective Equipment | 400569 - Overheating/Corrosion on HV Fuse connection point. (Identified from drone inspection)
|  | O-300751-H | Fert. Works |  | Kioreroa CB6 | 2026-02-12 08:51 | 46065.3685 | 2026-02-12 10:18 | 46065.4291 | 0.0013364 | 1.5361e-05 | 1 | 87 | Planned | Planned Interruption | Attempted Repair oil leak. Could not lift Tx Kennel due to internal ceiling height. Job not completed.
|  | O-300919-H | Paparoa |  | Mareretu CB6 | 2026-02-12 09:09 | 46065.3811 | 2026-02-12 15:38 | 46065.6513 | 1.3765 | 0.0036867 | 240 | 89609 | Planned | Planned Interruption | Repalce Poles, cross-arms and hardwares
|  | F-300799-H | Paparoa |  | Mareretu CB6 | 2026-02-12 11:31 | 46065.4796 | 2026-02-12 11:48 | 46065.4914 | 0.092796 | 0.0054532 | 355 | 6041 | Unplanned | Unknown | 15 min close (excl Sw 353 - shutdown O-300919)
|  | F-300802-H | Parua Bay |  | Parua Bay CB2 | 2026-02-12 16:30 | 46065.6872 | 2026-02-12 18:52 | 46065.7863 | 0.035069 | 0.00024578 | 16 | 2283 | Unplanned | Defective Equipment | 400625 - Replace broken DDO's Tx OO238, cracked/broken insulator on DDO
|  | F-300808-H | Paparoa |  | Mareretu CB6 | 2026-02-12 16:48 | 46065.7003 | 2026-02-12 19:13 | 46065.8007 | 0.12542 | 0.0025039 | 163 | 8165 | Unplanned | Vegetation | 400626 - HV lines down @ pole 31598 caused by tree branch
|  | F-300805-H | North Dargaville |  | Dargaville CB1 | 2026-02-12 18:06 | 46065.7542 | 2026-02-12 18:53 | 46065.7868 | 0.065699 | 0.0013979 | 91 | 4277 | Unplanned | Defective Equipment | 400633 - Floating jumper on to LA's at Tx M537, HD connector come loose
|  | F-300814-H | Hakaru |  | Kaiwaka CB1032 | 2026-02-12 20:06 | 46065.8373 | 2026-02-13 03:54 | 46066.1625 | 1.4567 | 0.0072965 | 475 | 94828 | Unplanned | Third Party Interference | 400634 - Car vs pole (event# 4398395)
|  | O-300769-H | Langs Beach |  | Mangawhai North CB3 | 2026-02-13 09:01 | 46066.3757 | 2026-02-13 09:58 | 46066.4153 | 0.056913 | 0.00099847 | 65 | 3705 | Planned | Planned Interruption | Investigate cable sizes
|  | O-300421-H | Ararua |  | Mareretu CB2 | 2026-02-13 09:02 | 46066.3763 | 2026-02-13 14:08 | 46066.5888 | 1.3213 | 0.0043165 | 281 | 86019 | Planned | Planned Interruption | Replace poles, crossarms, hardware
|  | F-300817-H | North Dargaville |  | Dargaville CB1 | 2026-02-13 12:33 | 46066.5229 | 2026-02-13 13:20 | 46066.5556 | 0.029601 | 0.00062981 | 41 | 1927 | Unplanned | Defective Equipment | FP400645 Replaced binders
|  | F-300823-H | Matapouri |  | Ngunguru CB1032 | 2026-02-13 13:05 | 46066.5449 | 2026-02-13 13:21 | 46066.5565 | 0.14905 | 0.012304 | 801 | 9703 | Unplanned | Lightning | N/A. Remotely livened feeder. (Later report of pole on fire F-300844)
|  | F-300829-H | ToeToe Rd |  | Kioreroa CB7 | 2026-02-13 13:33 | 46066.5644 | 2026-02-13 13:51 | 46066.5767 | 0.067512 | 0.0094164 | 613 | 4395 | Unplanned | Lightning | Trip EF. FPIs at sw 10094 indicate Phase B & EF. Lightning event
|  | F-300835-H | Mata |  | Ruakaka CB3 | 2026-02-13 13:50 | 46066.5765 | 2026-02-13 13:51 | 46066.5772 | 0.0070661 | 0.0068357 | 445 | 460 | Unplanned | Lightning | FPIs' 503 activated, Not FPI's 559. Several Tx's had blown HV fuses
|  | F-300856-H | Mata |  | Ruakaka CB3 | 2026-02-13 14:55 | 46066.6215 | 2026-02-13 18:33 | 46066.7729 | 0.016744 | 7.6806e-05 | 5 | 1090 | Unplanned | Lightning | FP400663 3x HV fuses blown
|  | F-300820-H | Matapouri |  | Ngunguru CB1032 | 2026-02-13 15:12 | 46066.6331 | 2026-02-14 01:08 | 46067.0472 | 1.4004 | 0.0075423 | 491 | 91164 | Unplanned | Lightning | 400666 Replaced 3 x HV fuses and replaced jumper. Repairs delayed due to lightning storm
|  | F-300820-H | Ruatangata |  | Kamo CB6 | 2026-02-13 15:12 | 46066.6333 | 2026-02-13 17:18 | 46066.7208 | 0.22065 | 0.0017512 | 114 | 14364 | Unplanned | Defective Equipment | FP400646 Replaced 3 x HV DDO's Due to drone inspection hot spot
|  | F-300874-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-02-13 15:14 | 46066.6347 | 2026-02-13 21:38 | 46066.9014 | 0.011797 | 3.0722e-05 | 2 | 768 | Unplanned | Lightning | 2x HV fuses 7213 blown, also NP 184 HV fuse. Incl F-300871 outage time (NP184)
|  | F-300847-H | Mata |  | Ruakaka CB3 | 2026-02-13 17:09 | 46066.7146 | 2026-02-13 17:36 | 46066.7333 | 0.0008295 | 3.0722e-05 | 2 | 54 | Unplanned | Lightning | FP400663 3 x HV fuses blown
|  | F-300868-H | Kaiwaka Town |  | Kaiwaka CB1062 | 2026-02-13 20:10 | 46066.8405 | 2026-02-13 20:26 | 46066.8513 | 0.12338 | 0.0079263 | 516 | 8032 | Unplanned | Lightning | 15 min close - suspected lightning
|  | F-300877-H | Titoki |  | Poroti CB1032 | 2026-02-13 23:35 | 46066.9827 | 2026-02-14 05:58 | 46067.2486 | 0.12997 | 0.0019969 | 130 | 8461 | Unplanned | Third Party Interference | FP400680 Car vs pole - FENZ4399243
|  | F-300883-H | Matapouri |  | Ngunguru CB1032 | 2026-02-14 01:52 | 46067.0778 | 2026-02-14 12:20 | 46067.5139 | 0.02894 | 4.6083e-05 | 3 | 1884 | Unplanned | Lightning | 400681 3 x HV fuses blown at Sw 7164
|  | F-300895-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-02-14 13:58 | 46067.5821 | 2026-02-14 18:37 | 46067.7757 | 0.16439 | 0.019155 | 1247 | 10702 | Unplanned | Vegetation | FP400694 Dead tree fell into line - broken 1x 11kV conductor
|  | O-300865-H | Kamo B |  | Kensington CB7 | 2026-02-15 09:13 | 46068.384 | 2026-02-15 15:01 | 46068.6257 | 0.27797 | 0.00079878 | 52 | 18096 | Planned | Planned Interruption | Replace pole 16605 and install new Tx
|  | F-300901-H | Marua |  | Hikurangi CB1022 | 2026-02-15 09:14 | 46068.3847 | 2026-02-15 09:46 | 46068.4069 | 0.00098311 | 3.0722e-05 | 2 | 64 | Unplanned | Lightning | 400699 / Isolate HV fuses to remove L/A Tails due to lightning.
|  | O-300925-H | Tangowahine |  | Dargaville CB8 | 2026-02-16 09:05 | 46069.3788 | 2026-02-16 13:02 | 46069.5433 | 0.061844 | 0.00026114 | 17 | 4026 | Planned | Planned Interruption | Repalce cross-arms and hardware
|  | O-300826-H | Kaiatea |  | Ngunguru CB1072 | 2026-02-16 09:32 | 46069.3975 | 2026-02-16 14:32 | 46069.6053 | 1.094 | 0.0036559 | 238 | 71218 | Planned | Planned Interruption | Tree Clearing Work
|  | O-300721-H | Port Feeder |  | Bream Bay CB1110 | 2026-02-16 11:12 | 46069.4667 | 2026-02-16 16:59 | 46069.7076 | 0.015991 | 4.6083e-05 | 3 | 1041 | Planned | Planned Interruption | remove KL 5029
|  | O-301081-H | Paparoa |  | Mareretu CB6 | 2026-02-17 09:05 | 46070.3785 | 2026-02-17 13:54 | 46070.5792 | 0.6167 | 0.0022734 | 148 | 40147 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | O-300607-H | Puwera |  | Maungatapere CB7 | 2026-02-17 09:18 | 46070.3875 | 2026-02-17 15:04 | 46070.6277 | 0.10095 | 0.00029186 | 19 | 6572 | Planned | Planned Interruption | POLE AND HARDWARE REPLACEMENTS
|  | F-300922-H | Te Kopuru |  | Dargaville CB2 | 2026-02-17 11:19 | 46070.4715 | 2026-02-17 13:15 | 46070.5521 | 0.0053457 | 4.6083e-05 | 3 | 348 | Unplanned | Defective Equipment | FP 400629 - Repair broken guy wire. Isolated HV for safety
|  | O-301096-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-02-17 12:48 | 46070.533 | 2026-02-17 15:58 | 46070.6653 | 0.55431 | 0.0076345 | 497 | 36085 | Unplanned | Third Party Interference | FP 400784 - LV lines down from NP veg contracting. Dropped HV for safety
|  | F-300913-H | Te Kopuru |  | Dargaville CB2 | 2026-02-17 14:02 | 46070.5847 | 2026-02-17 16:31 | 46070.6882 | 0.15344 | 0.0010292 | 67 | 9989 | Unplanned | Defective Equipment | FP 400752 - Replaced x-arm
|  | O-301027-H | Titoki |  | Poroti CB1032 | 2026-02-18 09:25 | 46071.3924 | 2026-02-18 14:18 | 46071.5958 | 0 | 0 | 0 | 0 | Planned | Planned Interruption | REPLACE POLES, REMOVE Tx W301, RELOCATE & REPLACE WITH NEW Tx w585
|  | O-300889-H | Marua |  | Hikurangi CB1022 | 2026-02-18 09:38 | 46071.4014 | 2026-02-18 15:05 | 46071.6285 | 0.095439 | 0.00029186 | 19 | 6213 | Planned | Planned Interruption | Tree Clearing Work
|  | O-301087-H | Paparoa |  | Mareretu CB6 | 2026-02-19 09:05 | 46072.3785 | 2026-02-19 16:10 | 46072.6736 | 0.93395 | 0.0022734 | 148 | 60800 | Planned | Planned Interruption | Reconductor - Late restoration due to workload.
|  | O-300424-H | Turiwiri |  | Dargaville CB9 | 2026-02-19 09:24 | 46072.3917 | 2026-02-19 14:42 | 46072.6125 | 0.35418 | 0.0011521 | 75 | 23057 | Planned | Planned Interruption | Replace Poles
|  | F-300949-H | Access Rd |  | Ruawai CB1022 | 2026-02-19 13:58 | 46072.582 | 2026-02-19 14:16 | 46072.5943 | 0.086975 | 0.0051152 | 333 | 5662 | Unplanned | Unknown | Trip EF - 15 min close, Phase A involved. No FPI Flagged
|  | O-300706-H | Tamaterau |  | Onerahi CB7 | 2026-02-20 09:01 | 46073.3757 | 2026-02-20 14:28 | 46073.6028 | 1.1101 | 0.0033948 | 221 | 72267 | Planned | Planned Interruption | 11kV Reconductoring
|  | O-300892-H | Otonga |  | Hikurangi CB1032 | 2026-02-20 09:37 | 46073.4007 | 2026-02-20 12:54 | 46073.5375 | 0.11802 | 0.00059908 | 39 | 7683 | Planned | Planned Interruption | Tree Clearing Work
|  | F-300952-H | Tangowahine |  | Dargaville CB8 | 2026-02-21 10:26 | 46074.4347 | 2026-02-21 14:17 | 46074.5951 | 0.011229 | 0.00016897 | 11 | 731 | Unplanned | Defective Equipment | 400912 Replace HV Fuses
|  | F-300955-H | North Kaiwaka |  | Kaiwaka CB1022 | 2026-02-21 21:28 | 46074.8943 | 2026-02-22 07:50 | 46075.3264 | 0.7859 | 0.009616 | 626 | 51162 | Unplanned | Wildlife | FP 400920 Install & remove Temp Break to repair Lines down
|  | O-300412-H | Tangowahine |  | Dargaville CB8 | 2026-02-23 09:02 | 46076.3763 | 2026-02-23 14:44 | 46076.6138 | 0.24163 | 0.00070661 | 46 | 15730 | Planned | Planned Interruption | Replace poles, crossarms and hardware
|  | O-301183-H | Paparoa |  | Mareretu CB6 | 2026-02-24 09:02 | 46077.3764 | 2026-02-24 15:31 | 46077.6465 | 0.86663 | 0.0022734 | 148 | 56417 | Planned | Planned Interruption | Replace poles and crossarms and straighten poles
|  | O-300868-H | Three Mile Bush |  | Kamo CB3 | 2026-02-25 08:35 | 46078.3576 | 2026-02-25 17:02 | 46078.7097 | 0.59968 | 0.0011828 | 77 | 39039 | Planned | Planned Interruption | Remove Switch 7342-7343-7344 Replace with new Switch.
|  | O-300946-H | Titoki |  | Poroti CB1032 | 2026-02-25 09:00 | 46078.375 | 2026-02-25 13:36 | 46078.5667 | 0.059355 | 0.00021506 | 14 | 3864 | Planned | Planned Interruption | Replace Poles, crossarms & hardwares Replace and upgrade transformers
|  | O-301315-H | Tangowahine |  | Dargaville CB8 | 2026-02-25 09:33 | 46078.3979 | 2026-02-25 13:43 | 46078.5715 | 0.24962 | 0.00099847 | 65 | 16250 | Planned | Planned Interruption | Replace LV conductor under HV lines
|  | F-300976-H | Tangaihi |  | Ruawai CB1032 | 2026-02-25 14:24 | 46078.5997 | 2026-02-25 22:25 | 46078.934 | 0.011229 | 0.00015361 | 10 | 731 | Unplanned | Defective Equipment | NF62632 - 2 faults - Replaced faulty LV fuses boxes that welded shut. - Replaced 1x ampact from main line to top of DDOs K306
|  | F-300979-H | Tikipunga Hill |  | Tikipunga CB4 | 2026-02-25 18:40 | 46078.7778 | 2026-02-25 19:37 | 46078.8174 | 0.014009 | 0.00024578 | 16 | 912 | Unplanned | Defective Equipment | NF62639 - Repaired spragged HV line
|  | F-300982-H | North River |  | Ruakaka CB7 | 2026-02-25 23:57 | 46078.9978 | 2026-02-26 01:07 | 46079.0463 | 0.14803 | 0.0021198 | 138 | 9637 | Unplanned | Third Party Interference | NF62645 - Car vs. Private pole. Customer reported LV lines on ground sparking, remotely switched for safety.
|  | O-300901-H | Tangowahine |  | Dargaville CB8 | 2026-02-26 08:31 | 46079.355 | 2026-02-26 16:21 | 46079.6813 | 0.021659 | 4.6083e-05 | 3 | 1410 | Planned | Planned Interruption | Install 66kV poles
|  | O-301264-H | Paparoa |  | Mareretu CB6 | 2026-02-26 09:01 | 46079.3757 | 2026-02-26 13:58 | 46079.5819 | 0.65102 | 0.0022734 | 148 | 42381 | Planned | Planned Interruption | Network Renewal - Replace 8 spans of conductors
|  | F-300985-H | Mains Ave |  | Tikipunga CB2 | 2026-02-26 12:43 | 46079.5297 | 2026-02-26 20:06 | 46079.8373 | 0.66005 | 0.00149 | 97 | 42969 | Unplanned | Third Party Interference | NF62655 - Truck Vs pole 16328
|  | O-300709-H | Tamaterau |  | Onerahi CB7 | 2026-02-27 09:03 | 46080.3772 | 2026-02-27 16:20 | 46080.6807 | 1.4839 | 0.0033948 | 221 | 96599 | Planned | Planned Interruption | Replacing 11kv Conductor. Remove KL 9181
|  | F-301000-H | Paparoa |  | Mareretu CB6 | 2026-02-27 18:18 | 46080.7622 | 2026-02-27 21:00 | 46080.875 | 0.3686 | 0.0091399 | 595 | 23996 | Unplanned | Wildlife | NF62732 - 2x HV lines down between poles 21012 & 21013 - Bird strike
|  | F-301003-H | Te Kopuru |  | Dargaville CB2 | 2026-02-28 08:29 | 46081.3534 | 2026-02-28 08:45 | 46081.3645 | 0.14062 | 0.014685 | 956 | 9154 | Unplanned | Defective Equipment | Sw 2255 FPI indication. Livened Sw 2255 after 15 mins (Suspect caused by broken HV jumper K157 - (F-301006)
|  | O-300757-H | Fraser |  | Kioreroa CB5 | 2026-02-28 08:54 | 46081.371 | 2026-02-28 12:19 | 46081.5134 | 0.003149 | 1.5361e-05 | 1 | 205 | Planned | Planned Interruption | Repair oil leak LV bushing and neutral bushing
|  | F-301006-H | Te Kopuru |  | Dargaville CB2 | 2026-02-28 10:42 | 46081.4461 | 2026-02-28 12:46 | 46081.5319 | 0.034225 | 0.00056836 | 37 | 2228 | Unplanned | Defective Equipment | NF62735 Broken HV jumper & Rusted HV fuses - K157
|  | F-301015-H | Marsden Bay |  | Bream Bay CB1107 | 2026-02-28 22:43 | 46081.9465 | 2026-03-01 19:37 | 46082.8172 | 0.068587 | 0.00073733 | 48 | 4465 | Unplanned | Defective Equipment | NF62740 - UG cable from Links 5049 burnt out at crucifix (power on time logged from generation connected to Tx RO300).
|  | F-301018-H | Langs Beach |  | Mangawhai North CB3 | 2026-03-01 01:04 | 46082.0447 | 2026-03-01 01:20 | 46082.0554 | 0.11851 | 0.012464 | 812 | 7721 | Unplanned | Adverse Weather | Tripped B&C phase EF, closed in 15min
|  | O-300499-H | Hatea Drive |  | Tikipunga CB3 | 2026-03-01 08:36 | 46082.3583 | 2026-03-01 18:37 | 46082.7757 | 0.98634 | 0.0016424 | 107 | 64260 | Planned | Planned Interruption | New RMU install - Shut down ran overtime
|  | O-300982-H | Tangowahine |  | Dargaville CB8 | 2026-03-02 08:32 | 46083.3556 | 2026-03-02 16:10 | 46083.6736 | 0.02109 | 4.6048e-05 | 3 | 1374 | Planned | Planned Interruption | Install 66kV conductor over 11kV
|  | O-301033-H | Kokopu |  | Poroti CB1022 | 2026-03-02 09:01 | 46083.3758 | 2026-03-02 11:51 | 46083.4939 | 0.43615 | 0.0025633 | 167 | 28415 | Planned | Planned Interruption | Replace crossarm and hardware
|  | O-301108-H | Titoki |  | Poroti CB1032 | 2026-03-02 09:03 | 46083.3771 | 2026-03-02 14:50 | 46083.6181 | 0.020982 | 6.1397e-05 | 4 | 1367 | Planned | Planned Interruption | Replace Tx W188 and hardware
|  | O-301135-H | Tamaterau |  | Onerahi CB7 | 2026-03-02 09:11 | 46083.3829 | 2026-03-02 14:18 | 46083.5958 | 0.55995 | 0.0018266 | 119 | 36481 | Planned | Planned Interruption | Tree Clearing Work
|  | F-301021-H | Access Rd |  | Ruawai CB1022 | 2026-03-02 16:18 | 46083.6792 | 2026-03-02 18:23 | 46083.766 | 0.025633 | 0.00061397 | 40 | 1670 | Unplanned | Defective Equipment | NF62797 Jumper of top of HV fuses due to burnt out ampact
|  | F-301030-H | Titoki |  | Poroti CB1032 | 2026-03-02 21:57 | 46083.9144 | 2026-03-03 00:30 | 46084.0208 | 0.17408 | 0.0011358 | 74 | 11341 | Unplanned | Defective Equipment | NF62808 Broken 11kV line
|  | F-301039-H | Springs Flat |  | Kamo CB1 | 2026-03-03 15:58 | 46084.6656 | 2026-03-03 17:00 | 46084.7084 | 0.80715 | 0.015963 | 1040 | 52586 | Unplanned | Third Party Interference | NF62842 - Car vs. Pole - initial report was eastern side of road (11kV & 33kV) Switched for safety. Found it was LV pole 347169
|  | O-301009-H | Tangowahine |  | Dargaville CB8 | 2026-03-04 08:31 | 46085.3548 | 2026-03-04 15:40 | 46085.6529 | 0.019754 | 4.6048e-05 | 3 | 1287 | Planned | Planned Interruption | Install 66kV conductor
|  | O-301378-H | Treatment |  | Kioreroa CB2 | 2026-03-04 09:06 | 46085.3792 | 2026-03-04 12:46 | 46085.5319 | 0.0033768 | 1.5349e-05 | 1 | 220 | Planned | Planned Interruption | Downgrade Transformer WO310
|  | F-301054-H | Kaiwaka South |  | Kaiwaka CB1072 | 2026-03-04 10:32 | 46085.4388 | 2026-03-04 18:03 | 46085.7522 | 0.73909 | 0.0029777 | 194 | 48152 | Unplanned | Third Party Interference | NF62867 - Car vs Pole
|  | O-301210-H | Coast |  | Dargaville CB6 | 2026-03-05 08:36 | 46086.3587 | 2026-03-05 18:47 | 46086.7828 | 1.2672 | 0.0027168 | 177 | 82556 | Planned | Planned Interruption | - Remove Sw 2166 - Connect new 11KV line from Pole 912177-912904 through to Pole 61523
|  | O-300109-I | Paparoa |  | Mareretu CB6 | 2026-03-05 09:06 | 46086.3792 | 2026-03-05 17:57 | 46086.7479 | 1.1231 | 0.0028243 | 184 | 73168 | Planned | Planned Interruption | Replace pole, cross-arms and hardware
|  | O-301381-H | Treatment |  | Kioreroa CB2 | 2026-03-05 09:07 | 46086.3799 | 2026-03-05 13:00 | 46086.5417 | 0.0035764 | 1.5349e-05 | 1 | 233 | Planned | Planned Interruption | Downgrade Tx
|  | O-301213-H | North Dargaville |  | Dargaville CB1 | 2026-03-06 09:04 | 46087.3781 | 2026-03-06 15:08 | 46087.6306 | 0.44637 | 0.0012279 | 80 | 29081 | Planned | Planned Interruption | Network Maintenance - Pole & x-arm replacements
|  | O-300964-H | Ararua |  | Mareretu CB2 | 2026-03-06 09:17 | 46087.3868 | 2026-03-06 14:02 | 46087.5847 | 2.0866 | 0.0073216 | 477 | 135945 | Planned | Planned Interruption | Replace poles, cross-arms & hardware
|  | F-301072-H | Taipuha |  | Mareretu CB1 | 2026-03-07 16:18 | 46088.679 | 2026-03-07 22:12 | 46088.925 | 0.17658 | 0.0036378 | 237 | 11504 | Unplanned | Defective Equipment | NF62991 - Loose hanging LV Neutral contact with HV jumper (Hi Lo Clash)
|  | F-301075-H | Waipu |  | Ruakaka CB2 | 2026-03-08 02:56 | 46089.1224 | 2026-03-08 07:43 | 46089.3215 | 0.73939 | 0.0025787 | 168 | 48171 | Unplanned | Defective Equipment | NF62993 - HV Line down (Center phase). Broke away at top of insulator.
|  | O-300058-I | Treatment |  | Kioreroa CB2 | 2026-03-08 08:38 | 46089.3597 | 2026-03-08 15:51 | 46089.6604 | 0.026585 | 6.1397e-05 | 4 | 1732 | Planned | Planned Interruption | Replace Tx WO185, pole and hardware
|  | O-300898-H | Paranui |  | Tikipunga CB6 | 2026-03-08 08:44 | 46089.3639 | 2026-03-08 14:57 | 46089.6229 | 0.0057252 | 1.5349e-05 | 1 | 373 | Planned | Planned Interruption | Oil leak repair & maintainance of transformer
|  | O-301045-H | Tangowahine |  | Dargaville CB8 | 2026-03-09 08:32 | 46090.3556 | 2026-03-09 13:52 | 46090.5776 | 0.01472 | 4.6048e-05 | 3 | 959 | Planned | Planned Interruption | Install 66kV conductor
|  | O-300118-I | Paparoa |  | Mareretu CB6 | 2026-03-10 08:20 | 46091.3472 | 2026-03-10 14:56 | 46091.6222 | 0.25676 | 0.0050959 | 332 | 16728 | Planned | Planned Interruption | Pole, hardware and conducor replacement. GEN beyond pole 915338
|  | O-300418-H | Te Kopuru |  | Dargaville CB2 | 2026-03-10 09:28 | 46091.3944 | 2026-03-10 14:50 | 46091.6181 | 0.079079 | 0.00024559 | 16 | 5152 | Planned | Planned Interruption | Upgrade Tx, reaplce cross-arms and hardwares
|  | F-301078-H | Brynderwyn |  | Maungaturoto CB1 | 2026-03-10 12:01 | 46091.5007 | 2026-03-10 19:25 | 46091.809 | 0.2868 | 0.0030084 | 196 | 18685 | Unplanned | Third Party Interference | NF63073 - Digger struck overhead lines btwn Pole 49805 & 49806. Replaced TX from damage.
|  | F-301081-H | Onoke |  | Kamo CB8 | 2026-03-10 16:23 | 46091.6828 | 2026-03-11 03:14 | 46092.1344 | 2.4823 | 0.023054 | 1502 | 161719 | Unplanned | Third Party Interference | NF63088 - Car Vs Pole. Installed temp break @ Pole 904493.
|  | F-301084-H | Tamaterau |  | Onerahi CB7 | 2026-03-10 21:01 | 46091.8759 | 2026-03-11 04:24 | 46092.1836 | 1.2331 | 0.017222 | 1568 | 80673 | Unplanned | Adverse Weather | NF63093 - AB ph OC. Portable FPIs @ Pole 51812 activated. Install Temp Break @ Pole 51832. Switching on F-301087-H & F-301084-H
|  | F-301093-H | Langs Beach |  | Mangawhai North CB3 | 2026-03-11 08:23 | 46092.3493 | 2026-03-11 08:39 | 46092.3603 | 0.17101 | 0.012464 | 812 | 11141 | Unplanned | Defective Equipment | Trip EF / A Phase Involved. FPI indication at sw 8090. 15 Min closed feeder (F4). Fault found in 2nd tripping (broken x-arm)
|  | O-301150-H | Titoki |  | Poroti CB1032 | 2026-03-11 09:12 | 46092.3833 | 2026-03-11 15:49 | 46092.659 | 1.3188 | 0.0034075 | 222 | 85919 | Planned | Planned Interruption | Replace poles, Tx, conductors and hardware - Slightly delayed restoration to perform functional test on recloser
|  | F-301096-H | Langs Beach |  | Mangawhai North CB3 | 2026-03-11 09:12 | 46092.3835 | 2026-03-11 18:02 | 46092.7514 | 1.0189 | 0.026815 | 1870 | 66503 | Unplanned | Defective Equipment | NF63119 - Recurring tripping that went back in. Found Broken X arm at pole 10688. Replaced BTN
|  | F-301102-H | Marsden Pt |  | Ruakaka CB1 | 2026-03-11 14:32 | 46092.6056 | 2026-03-11 20:26 | 46092.8514 | 1.2411 | 0.03868 | 2520 | 80858 | Unplanned | Defective Equipment | Corroded connector - Jumper to the HV bushing of the Tx blown off NF63122
|  | F-301105-H | POR - WAI - MPEN |  | Maungatapere POS CB1312 | 2026-03-11 19:21 | 46092.8064 | 2026-03-12 03:18 | 46093.1372 | 0.52284 | 0.0053876 | 351 | 34063 | Unplanned | Third Party Interference | NF63133 Car vs pole M'kahia Rd 33KV/11KV
|  | O-301054-H | Tangowahine |  | Dargaville CB8 | 2026-03-12 08:39 | 46093.3604 | 2026-03-12 15:56 | 46093.6637 | 0.020107 | 4.6048e-05 | 3 | 1310 | Planned | Planned Interruption | Install 66kV conductor
|  | O-300121-I | Paparoa |  | Mareretu CB6 | 2026-03-12 08:55 | 46093.3715 | 2026-03-12 16:06 | 46093.6708 | 1.4193 | 0.0034689 | 226 | 92465 | Planned | Planned Interruption | Replace poles, crossarms and conductor Delay due to 1 x IASM left on the line - burnt line down
|  | F-301111-H | Taipuha |  | Mareretu CB1 | 2026-03-12 12:28 | 46093.5197 | 2026-03-12 13:26 | 46093.5597 | 0.10846 | 0.007122 | 464 | 7066 | Unplanned | Defective Equipment | NF63153 - Broken jumper @ crucifix. MTU CB 1 showing 0A
|  | F-301117-H | Paparoa |  | Mareretu CB6 | 2026-03-12 14:34 | 46093.6069 | 2026-03-12 14:40 | 46093.6109 | 0.032755 | 0.0056639 | 369 | 2134 | Unplanned | Human Error | Tripping caused by livening line with earth still in place on S-300381-H.
|  | O-300967-H | Ararua |  | Mareretu CB2 | 2026-03-13 09:04 | 46094.3778 | 2026-03-13 12:17 | 46094.5118 | 1.4101 | 0.0073062 | 476 | 91868 | Planned | Planned Interruption | Network Maintenance - replace poles, crossarms and hardware
|  | F-301126-H | Hakaru |  | Kaiwaka CB1032 | 2026-03-14 14:52 | 46095.6197 | 2026-03-14 15:08 | 46095.6303 | 0.19876 | 0.013062 | 851 | 12949 | Unplanned | Unknown | A&B phase O/C - Unknown cause, F4 closed in 15mins
|  | F-301129-H | Kaka St |  | Whangarei South CB1032 | 2026-03-14 16:56 | 46095.7057 | 2026-03-14 17:18 | 46095.7209 | 0.081612 | 0.0057099 | 372 | 5317 | Unplanned | Vegetation | NF63215 - A&B phase O/C. Palm tree branch on lines Cnr of Albert St & Woods Rd
|  | O-301309-H | Thelma Road |  | Mangawhai North CB4 | 2026-03-15 09:08 | 46096.3808 | 2026-03-15 10:48 | 46096.4497 | 0.46761 | 0.0047122 | 307 | 30465 | Planned | Planned Interruption | Install new switch 10247
|  | F-301138-H | Puwera |  | Maungatapere CB7 | 2026-03-16 08:35 | 46097.3576 | 2026-03-16 08:51 | 46097.3686 | 0.11458 | 0.0071834 | 468 | 7465 | Unplanned | Unknown | 15 min close - O/C B&C
|  | O-301222-H | Titoki |  | Poroti CB1032 | 2026-03-16 09:15 | 46097.3856 | 2026-03-16 15:11 | 46097.6326 | 0.049133 | 0.00013814 | 9 | 3201 | Planned | Planned Interruption | Replace 11kV pole & crossarms
|  | F-301153-H | Jordan Valley |  | Hikurangi CB1102 | 2026-03-16 18:21 | 46097.7649 | 2026-03-16 19:01 | 46097.7923 | 0.00061397 | 1.5349e-05 | 1 | 40 | Unplanned | Unknown | NF63271 - Found fuse links 602 x2 blown, opened 3rd fuse, patrolled, found nothing, closed in and holding - Unknown
|  | F-301156-H | Whau Valley |  | Tikipunga CB1 | 2026-03-17 05:47 | 46098.2412 | 2026-03-17 07:32 | 46098.3139 | 0.2332 | 0.019739 | 1286 | 15193 | Unplanned | Wildlife | NF63272 / Feeder de-energised for safety until Tx fuses isolated (loud noises in Tx). LV disconnect fault - Rat
|  | O-301057-H | Tangowahine |  | Dargaville CB8 | 2026-03-17 08:33 | 46098.3566 | 2026-03-17 15:42 | 46098.6538 | 0.019708 | 4.6048e-05 | 3 | 1284 | Planned | Planned Interruption | Install 66kV & 11kV conductor
|  | O-300142-I | Paparoa |  | Mareretu CB6 | 2026-03-17 08:49 | 46098.3674 | 2026-03-17 15:47 | 46098.6576 | 0.41845 | 0.0062932 | 410 | 27262 | Planned | Planned Interruption | Pole, crossarms & conductor replacements. Delay on outage due to Gen contractor late. Delay on restoration/ pole hole issues.
|  | F-301171-H | Tangowahine |  | Dargaville CB8 | 2026-03-18 08:30 | 46099.3543 | 2026-03-18 08:49 | 46099.3676 | 0.14553 | 0.0088565 | 577 | 9481 | Unplanned | Unknown | Trip EF - Unknown
|  | O-301225-H | Titoki |  | Poroti CB1032 | 2026-03-18 09:05 | 46099.3782 | 2026-03-18 17:24 | 46099.7249 | 0.099616 | 0.00019954 | 13 | 6490 | Planned | Planned Interruption | Replace poles and conductor - Delayed restoration due to Pole hole issues & Conductor installation problems
|  | O-301330-H | Swamp North |  | Hikurangi CB1042 | 2026-03-18 09:10 | 46099.3819 | 2026-03-18 15:21 | 46099.6396 | 0.26764 | 0.00072141 | 47 | 17437 | Planned | Planned Interruption | Install new tx and clear trees
|  | F-301183-H | Paranui |  | Tikipunga CB6 | 2026-03-18 19:39 | 46099.8187 | 2026-03-18 21:56 | 46099.9139 | 0.037851 | 0.00027629 | 18 | 2466 | Unplanned | Defective Equipment | NF63355 - Replaced broken pole found by drone inspection.
|  | O-301168-H | Tangowahine |  | Dargaville CB8 | 2026-03-19 08:31 | 46100.3551 | 2026-03-19 17:02 | 46100.7094 | 1.3469 | 0.0027629 | 180 | 87750 | Planned | Planned Interruption | Reconfigure 11kV lines to Tx
|  | O-300178-I | Paparoa |  | Mareretu CB6 | 2026-03-19 08:44 | 46100.3639 | 2026-03-19 14:02 | 46100.5847 | 1.0497 | 0.0034689 | 226 | 68391 | Planned | Planned Interruption | upgrade conductors
|  | O-300085-I | Swamp North |  | Hikurangi CB1042 | 2026-03-19 09:49 | 46100.409 | 2026-03-19 15:21 | 46100.6396 | 0.076439 | 0.00023024 | 15 | 4980 | Planned | Planned Interruption | tree clearing works & Tx KB309 Inspection.
|  | O-300211-I | Cartwright Rd |  | Onerahi CB6 | 2026-03-19 10:23 | 46100.4326 | 2026-03-19 14:58 | 46100.6236 | 0.3208 | 0.0011665 | 76 | 20900 | Planned | Planned Interruption | Install new pole 916237
|  | F-301186-H | Whangarei Heads |  | Parua Bay CB3 | 2026-03-19 11:04 | 46100.4608 | 2026-03-19 11:19 | 46100.4714 | 0.18574 | 0.012264 | 799 | 12101 | Unplanned | Unknown | Overcurrent trip B & C. 15 Min Close & BTN
|  | F-301192-H | North Dargaville |  | Dargaville CB1 | 2026-03-19 17:15 | 46100.7185 | 2026-03-19 17:31 | 46100.7298 | 0.049332 | 0.0030238 | 197 | 3214 | Unplanned | Unknown | Trip to lockout while fed from CB6 DAR due to NAR13373 & 15 min closed. BTN
|  | O-300106-I | Titoki |  | Poroti CB1032 | 2026-03-20 09:11 | 46101.3826 | 2026-03-20 12:56 | 46101.5389 | 0.0034536 | 1.5349e-05 | 1 | 225 | Planned | Planned Interruption | Replace Tx, cross-arms and hardware
|  | O-300223-I | Tangowahine |  | Dargaville CB8 | 2026-03-20 09:32 | 46101.3972 | 2026-03-20 13:05 | 46101.5451 | 0.068657 | 0.00032233 | 21 | 4473 | Planned | Planned Interruption | Replace pole
|  | O-301273-H | Titoki |  | Poroti CB1032 | 2026-03-20 09:45 | 46101.4062 | 2026-03-20 14:37 | 46101.609 | 0.017636 | 6.1397e-05 | 4 | 1149 | Planned | Planned Interruption | Replace crossarms and conductor
|  | O-300199-I | Taipuha |  | Mareretu CB1 | 2026-03-20 10:05 | 46101.4201 | 2026-03-20 13:02 | 46101.5431 | 0.062487 | 0.00035303 | 23 | 4071 | Planned | Planned Interruption | Replace pole
|  | F-301201-H | Alamein Ave |  | Onerahi CB3 | 2026-03-20 15:48 | 46101.6584 | 2026-03-20 16:23 | 46101.6827 | 0.55018 | 0.015794 | 1029 | 35844 | Unplanned | Unknown | S-300423-H / When changing relay setting on CB3 ONE it cause a trip. Got ok from engineer to re close. BTN
|  | F-301207-H | North Dargaville |  | Dargaville CB1 | 2026-03-21 08:52 | 46102.3694 | 2026-03-21 10:22 | 46102.432 | 0.029378 | 0.00085955 | 56 | 1914 | Unplanned | Wildlife | NF63437 - HV line down at pole 27001, caused by possum.
|  | F-301216-H | Tangowahine |  | Dargaville CB8 | 2026-03-22 10:45 | 46103.4479 | 2026-03-22 11:54 | 46103.4957 | 0.12327 | 0.0031312 | 204 | 8031 | Unplanned | Third Party Interference | NF63445 - Tripped O/C B&C phase, Followed up customer call before livening regarding potential damage by digger.
|  | F-301219-H | Kokopu |  | Poroti CB1022 | 2026-03-22 14:14 | 46103.5928 | 2026-03-22 19:15 | 46103.8022 | 0.39176 | 0.0063392 | 413 | 25523 | Unplanned | Third Party Interference | NF63447 - Tractor vs HV lines x2 sites (pole 31209 to 31208 & pole 31211 to 31212)
|  | O-301279-H | Titoki |  | Poroti CB1032 | 2026-03-23 09:26 | 46104.3931 | 2026-03-23 14:55 | 46104.6217 | 0.11114 | 0.00033768 | 22 | 7241 | Planned | Planned Interruption | Replace pole, Tx & conductor
|  | F-301234-H | Wairere |  | Mareretu CB5 | 2026-03-23 17:35 | 46104.7325 | 2026-03-23 18:38 | 46104.7762 | 0.053154 | 0.00084421 | 55 | 3463 | Unplanned | Defective Equipment | NF63481 - replace broken insulators @ pole 21227 & 21240
|  | F-301237-H | Hakaru |  | Kaiwaka CB1032 | 2026-03-23 19:26 | 46104.81 | 2026-03-23 19:45 | 46104.8231 | 0.089102 | 0.013062 | 851 | 5805 | Unplanned | Unknown | Tripped B&C O/C, unknown cause
|  | O-300181-I | North Dargaville |  | Dargaville CB1 | 2026-03-24 08:31 | 46105.3549 | 2026-03-24 14:26 | 46105.6013 | 0.26 | 0.0062932 | 410 | 16939 | Planned | Planned Interruption | Network Renewal - Pole, crossarms & conductor replacements
|  | F-301252-H | Titoki |  | Poroti CB1032 | 2026-03-25 07:48 | 46106.325 | 2026-03-25 09:38 | 46106.4014 | 0.016884 | 0.00015349 | 10 | 1100 | Unplanned | Wildlife | NF/63537 - x2 Blown HV Fuses. Possible Bird cause (lines above pond)
|  | O-300193-I | Pataua |  | Parua Bay CB1 | 2026-03-25 09:38 | 46106.4012 | 2026-03-25 11:51 | 46106.4937 | 0.21678 | 0.001627 | 106 | 14123 | Planned | Planned Interruption | Re-sag HV & LV lines
|  | F-301270-H | Tamaterau |  | Onerahi CB7 | 2026-03-25 13:46 | 46106.5736 | 2026-03-25 14:47 | 46106.616 | 0.076454 | 0.0013814 | 90 | 4981 | Unplanned | Other Cause | NF63555/ Remove temp break pole 51832 (Original previous intermittent fault on feeder not found, no subsequent trips)
|  | F-301276-H | Tangowahine |  | Dargaville CB8 | 2026-03-25 15:43 | 46106.6547 | 2026-03-25 23:01 | 46106.959 | 0.43696 | 0.011205 | 730 | 28468 | Unplanned | Defective Equipment | NF63570 - Repaired HV conductor and lowered crossarm for clearance
|  | F-301282-H | North Dargaville |  | Dargaville CB1 | 2026-03-25 19:28 | 46106.8114 | 2026-03-26 11:11 | 46107.466 | 1.0912 | 0.0040215 | 262 | 71091 | Unplanned | Defective Equipment | NF63575/ Wraplock binder corrosion at HV Pins
|  | F-301279-H | North Dargaville |  | Dargaville CB1 | 2026-03-25 20:16 | 46106.8444 | 2026-03-26 10:58 | 46107.4569 | 0.45529 | 0.0023331 | 152 | 29662 | Unplanned | Defective Equipment | NF63577 - Repaired HV lines down - Cause not clear, Possible clash or tree debris. High winds and High rain.
|  | F-301288-H | Whakapara |  | Hikurangi CB1112 | 2026-03-25 20:57 | 46106.873 | 2026-03-26 04:57 | 46107.2063 | 1.8341 | 0.022134 | 1442 | 119490 | Unplanned | Defective Equipment | NF63578 - Replaced broken crossarm & lines down
|  | F-301291-H | Matapouri |  | Ngunguru CB1032 | 2026-03-25 21:48 | 46106.9084 | 2026-03-25 22:07 | 46106.9212 | 0.21819 | 0.01231 | 802 | 14215 | Unplanned | Adverse Weather | A & B OC. No FPIs @ SW 721
|  | F-301294-H | Ruatangata |  | Kamo CB6 | 2026-03-25 22:07 | 46106.9218 | 2026-03-25 23:37 | 46106.984 | 0.39173 | 0.01145 | 746 | 25521 | Unplanned | Adverse Weather | NF63580 - Reports of loud bang & sparks bottom of Parakiore - no hard fault found.
|  | F-301300-H | North River |  | Ruakaka CB7 | 2026-03-26 00:03 | 46107.0024 | 2026-03-26 05:50 | 46107.2431 | 0.49586 | 0.0076592 | 633 | 32417 | Unplanned | Vegetation | NF63581 - Clear tree from lines
|  | F-301306-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-03-26 02:39 | 46107.1105 | 2026-03-26 03:18 | 46107.1375 | 0.30592 | 0.010299 | 671 | 19931 | Unplanned | Adverse Weather | SW 10332 FPIs A,B & C
|  | F-301309-H | North Dargaville |  | Dargaville CB1 | 2026-03-26 02:40 | 46107.1112 | 2026-03-26 03:17 | 46107.1369 | 0.28749 | 0.0082425 | 537 | 18730 | Unplanned | Adverse Weather | T & C after 15 mins. Recl 1540 tripped at same time. Excludes Sw 3140 (open on F-301282)
|  | F-301315-H | Coast |  | Dargaville CB6 | 2026-03-26 03:42 | 46107.1545 | 2026-03-26 13:34 | 46107.5653 | 0.58069 | 0.0033922 | 221 | 37832 | Unplanned | Vegetation | NF63582 - HV Lines down between Pole 55406 & Pole 55407
|  | F-301318-H | Tutukaka Block |  | Ngunguru CB1082 | 2026-03-26 06:37 | 46107.2759 | 2026-03-26 15:55 | 46107.6633 | 3.1526 | 0.0076899 | 501 | 205389 | Unplanned | Vegetation | NF63588/ HV Line down mid span. faultman reported vegetation likely cause. Line was on the ground and did not trip.
|  | F-301321-H | Matapouri |  | Ngunguru CB1032 | 2026-03-26 08:43 | 46107.3634 | 2026-03-26 09:07 | 46107.3799 | 0.28138 | 0.01231 | 802 | 18332 | Unplanned | Adverse Weather | Trip OC Phase AB. Unknown, High winds and Heavy Rain
|  | F-301330-H | Ararua |  | Mareretu CB2 | 2026-03-26 09:31 | 46107.3966 | 2026-03-26 18:16 | 46107.7611 | 1.3263 | 0.013446 | 876 | 86408 | Unplanned | Defective Equipment | NF 63602 HV line clashed in wind & burnt down - didn't have a stagger - now it does. Hi Low clash
|  | F-301333-H | Mangawhai Heads |  | Mangawhai North CB1 | 2026-03-26 10:06 | 46107.4207 | 2026-03-26 18:52 | 46107.7861 | 0.2357 | 0.001274 | 83 | 15356 | Unplanned | Defective Equipment | NF 63593 Repair cable fault at crucifix
|  | F-301336-H | ToeToe Rd |  | Kioreroa CB7 | 2026-03-26 10:14 | 46107.4263 | 2026-03-26 14:10 | 46107.5903 | 0.41642 | 0.0094091 | 613 | 27130 | Unplanned | Vegetation | NF63604 Repair LV Lines down due to trees
|  | F-301342-H | North Dargaville |  | Dargaville CB1 | 2026-03-26 17:02 | 46107.7098 | 2026-03-26 17:22 | 46107.7234 | 0.059371 | 0.0030238 | 197 | 3868 | Unplanned | Adverse Weather | Trip OC Phase ABC
|  | F-301345-H | Titoki |  | Poroti CB1032 | 2026-03-26 17:45 | 46107.7398 | 2026-03-27 00:53 | 46108.0368 | 0.46631 | 0.0046662 | 304 | 30380 | Unplanned | Vegetation | NF 63640 Tree through lines pole 50657-50658
|  | O-300724-H | Parua Bay |  | Parua Bay CB2 | 2026-03-27 09:01 | 46108.3757 | 2026-03-27 15:30 | 46108.6458 | 0.8598 | 0.0022103 | 144 | 56016 | Planned | Planned Interruption | Replace pole and hardware, Install new Tx
|  | O-300343-I | Puwera |  | Maungatapere CB7 | 2026-03-27 09:03 | 46108.3774 | 2026-03-27 14:43 | 46108.6134 | 0.099094 | 0.00029163 | 19 | 6456 | Planned | Planned Interruption | Install new Tx
|  | F-301366-H | North River |  | Ruakaka CB7 | 2026-03-27 19:55 | 46108.8299 | 2026-03-28 01:59 | 46109.0826 | 0.42682 | 0.0057406 | 374 | 27807 | Unplanned | Vegetation | NF63692 - FENZ call for trees burning from lines. De-energised remotely - installed Temp Break & Cleared trees. Reinstated
|  | F-301369-H | Ruawai Town |  | Ruawai CB1072 | 2026-03-27 23:49 | 46108.9925 | 2026-03-28 00:06 | 46109.0038 | 0.038987 | 0.0049578 | 323 | 2540 | Unplanned | Unknown | T & C > 15mins, A & B FPIs @ SW 2078
|  | F-301372-H | Pataua |  | Parua Bay CB1 | 2026-03-28 18:49 | 46109.7842 | 2026-03-28 20:08 | 46109.8386 | 1.1363 | 0.014751 | 961 | 74033 | Unplanned | Wildlife | NF63710 Unable to backfeed FPI switches due to operational restriction. Removed bird & relivened
|  | F-301381-H | Walton St |  | Whangarei South CB1022 | 2026-03-29 02:03 | 46110.0854 | 2026-03-29 15:41 | 46110.6535 | 1.3225 | 0.0066922 | 436 | 86161 | Unplanned | Third Party Interference | NF63713 - Car Vs pole 35633 (Temp break installed)
|  | O-300073-I | Te Kopuru |  | Dargaville CB2 | 2026-03-30 09:08 | 46111.3806 | 2026-03-30 15:32 | 46111.6472 | 0.035365 | 9.2095e-05 | 6 | 2304 | Planned | Planned Interruption | Pole changes
|  | O-300145-I | Dunns Rd |  | Ruawai CB1082 | 2026-03-30 09:15 | 46111.3854 | 2026-03-30 16:03 | 46111.6687 | 0.11272 | 0.00027629 | 18 | 7344 | Planned | Planned Interruption | Network Maintenance - X-arm & pole changes
|  | O-300862-H | Otonga |  | Hikurangi CB1032 | 2026-03-30 09:21 | 46111.3896 | 2026-03-30 14:40 | 46111.6111 | 0.21544 | 0.00067536 | 44 | 14036 | Planned | Planned Interruption | Upgrade tx and pole hardware
|  | F-301384-H | Tangowahine |  | Dargaville CB8 | 2026-03-30 10:46 | 46111.4483 | 2026-03-30 14:27 | 46111.6021 | 0.22499 | 0.0031005 | 202 | 14658 | Unplanned | Defective Equipment | Fault caused by HV line falling from deadend during LL works at Sw 2209
|  | F-301387-H | Fert. Works |  | Kioreroa CB6 | 2026-03-30 13:26 | 46111.5597 | 2026-03-30 14:01 | 46111.584 | 0.0010744 | 3.0698e-05 | 2 | 70 | Unplanned | Defective Equipment | NF63733 - opened to test/check HV fuses due to local high readings @ Tx WO207 - Later replaced Tx (F-301390-H)
|  | F-301390-H | Fert. Works |  | Kioreroa CB6 | 2026-03-30 15:41 | 46111.6535 | 2026-03-30 17:50 | 46111.7431 | 0.0039601 | 3.0698e-05 | 2 | 258 | Unplanned | Defective Equipment | NF63733 - Replace Tx WO207
|  | F-301393-H | Tamaterau |  | Onerahi CB7 | 2026-03-30 20:28 | 46111.853 | 2026-03-30 22:29 | 46111.9365 | 0.39082 | 0.0086109 | 561 | 25462 | Unplanned | Unknown | NF63782 / Trip B phase overcurrent. Large Explosion reported near substation, patrolled but nothing found. BTN
|  | O-300388-I | Paparoa |  | Mareretu CB6 | 2026-03-31 08:22 | 46112.3489 | 2026-03-31 15:05 | 46112.6285 | 0.15701 | 0.0071527 | 466 | 10229 | Planned | Planned Interruption | Pole, crossarms & conductor replacements
|  | O-301084-H | Titoki |  | Poroti CB1032 | 2026-03-31 09:25 | 46112.3926 | 2026-03-31 14:27 | 46112.6021 | 0.027782 | 9.2095e-05 | 6 | 1810 | Planned | Planned Interruption | Replace pole & TX W306
|  | F-301396-H | North Dargaville |  | Dargaville CB1 | 2026-03-31 15:18 | 46112.6373 | 2026-03-31 20:42 | 46112.8622 | 0.014919 | 4.6048e-05 | 3 | 972 | Unplanned | Defective Equipment | NF63795 - Replace broken X-arm
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27 |  | ¹ Extend table as necessary to disclose information for all individual interruptions